## Sheet1
filename | workorder_no | json_data
PS_PM_QTR_UPSSystem_4000672868.pdf | 4000672868 | {"station": "MAH", "date_time": "16/04/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": null, "general_inspection.readings.A_battery_capacity": null, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": null, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": null, "general_inspection.readings.F_battery_voltage_v.negative": null, "general_inspection.readings.G_battery_charge_car.positive": null, "general_inspection.readings.G_battery_charge_car.negative": null, "general_inspection.readings.H_discharge_current": null, "general_inspection.readings.I_rectifier_voltage.a": null, "general_inspection.readings.I_rectifier_voltage.b": null, "general_inspection.readings.I_rectifier_voltage.c": null, "general_inspection.readings.J_bypass_voltage.a": null, "general_inspection.readings.J_bypass_voltage.b": null, "general_inspection.readings.J_bypass_voltage.c": null, "general_inspection.readings.K_output_voltage.a": null, "general_inspection.readings.K_output_voltage.b": null, "general_inspection.readings.K_output_voltage.c": null, "general_inspection.readings.L_output_current.a": null, "general_inspection.readings.L_output_current.b": null, "general_inspection.readings.L_output_current.c": null, "general_inspection.readings.M_active_power.a": null, "general_inspection.readings.M_active_power.b": null, "general_inspection.readings.M_active_power.c": null, "general_inspection.readings.N_reactive_power.a": null, "general_inspection.readings.N_reactive_power.b": null, "general_inspection.readings.N_reactive_power.c": null, "general_inspection.readings.O_apparent_power.a": null, "general_inspection.readings.O_apparent_power.b": null, "general_inspection.readings.O_apparent_power.c": null, "general_inspection.readings.P_output_power.a": null, "general_inspection.readings.P_output_power.b": null, "general_inspection.readings.P_output_power.c": null, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": true, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All in good condition", "technician_name": "IZZUDDIN", "technician_id": 22388, "supervisor_name": "MOHD IRZAN", "supervisor_id": 7094}
PS_PM_QTR_UPSSystem_4000672871.pdf | 4000672871 | {"station": "MKU", "date_time": "22/04/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": null, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 37.9, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 261.0, "general_inspection.readings.D_output_frequency": 50.06, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 268.0, "general_inspection.readings.F_battery_voltage_v.negative": 249.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 233.0, "general_inspection.readings.I_rectifier_voltage.b": 234.0, "general_inspection.readings.I_rectifier_voltage.c": 237.0, "general_inspection.readings.J_bypass_voltage.a": 235.0, "general_inspection.readings.J_bypass_voltage.b": 264.0, "general_inspection.readings.J_bypass_voltage.c": 237.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.4, "general_inspection.readings.L_output_current.b": 4.3, "general_inspection.readings.L_output_current.c": 3.6, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.2, "general_inspection.readings.M_active_power.c": 0.2, "general_inspection.readings.N_reactive_power.a": 0.3, "general_inspection.readings.N_reactive_power.b": 1.0, "general_inspection.readings.N_reactive_power.c": 0.9, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.0, "general_inspection.readings.O_apparent_power.c": 0.9, "general_inspection.readings.P_output_power.a": 4.0, "general_inspection.readings.P_output_power.b": 15.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": null, "servicing_and_cleaning.switch_on_maintenance_bypass.status": null, "servicing_and_cleaning.confirm_display_panel.status": null, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": null, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": "", "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": null, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": null, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": null, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": null, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": null, "battery_backup_test.turn_off_main_switch_breaker.status": null, "battery_backup_test.confirm_alarm_sounding.status": null, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": null, "battery_backup_test.switch_on_back_main_switch_breaker.status": null, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All in good condition", "technician_name": "M. ISKANDAR", "technician_id": 20157, "supervisor_name": "NORIEZUWADI", "supervisor_id": 19234}
PS_PM_QTR_UPSSystem_4000690941.pdf | 4000690941 | {"station": "DCC", "date_time": "26/07/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 98.7, "general_inspection.readings.B_module_temperature.min": 25.5, "general_inspection.readings.B_module_temperature.max": 27.0, "general_inspection.readings.C_battery_run_time": null, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 268.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.4, "general_inspection.readings.G_battery_charge_car.positive": null, "general_inspection.readings.G_battery_charge_car.negative": null, "general_inspection.readings.H_discharge_current": null, "general_inspection.readings.I_rectifier_voltage.a": null, "general_inspection.readings.I_rectifier_voltage.b": null, "general_inspection.readings.I_rectifier_voltage.c": null, "general_inspection.readings.J_bypass_voltage.a": 241.6, "general_inspection.readings.J_bypass_voltage.b": null, "general_inspection.readings.J_bypass_voltage.c": null, "general_inspection.readings.K_output_voltage.a": 240.4, "general_inspection.readings.K_output_voltage.b": null, "general_inspection.readings.K_output_voltage.c": null, "general_inspection.readings.L_output_current.a": 32.0, "general_inspection.readings.L_output_current.b": null, "general_inspection.readings.L_output_current.c": null, "general_inspection.readings.M_active_power.a": 8.4, "general_inspection.readings.M_active_power.b": null, "general_inspection.readings.M_active_power.c": null, "general_inspection.readings.N_reactive_power.a": 9.1, "general_inspection.readings.N_reactive_power.b": null, "general_inspection.readings.N_reactive_power.c": null, "general_inspection.readings.O_apparent_power.a": 9.0, "general_inspection.readings.O_apparent_power.b": null, "general_inspection.readings.O_apparent_power.c": null, "general_inspection.readings.P_output_power.a": 30.3, "general_inspection.readings.P_output_power.b": null, "general_inspection.readings.P_output_power.c": null, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": true, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "IN GOOD CONDITION", "technician_name": "M. ISKANDAR", "technician_id": 20157, "supervisor_name": "NORIEZUWADI", "supervisor_id": 19234}
PS_PM_QTR_UPSSystem_4000672874.pdf | 4000672874 | {"station": "HAH", "date_time": "17/04/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 36.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 352.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 2.67, "general_inspection.readings.F_battery_voltage_v.negative": 2.67, "general_inspection.readings.G_battery_charge_car.positive": null, "general_inspection.readings.G_battery_charge_car.negative": null, "general_inspection.readings.H_discharge_current": null, "general_inspection.readings.I_rectifier_voltage.a": 240.0, "general_inspection.readings.I_rectifier_voltage.b": 239.0, "general_inspection.readings.I_rectifier_voltage.c": 242.0, "general_inspection.readings.J_bypass_voltage.a": 241.0, "general_inspection.readings.J_bypass_voltage.b": 239.0, "general_inspection.readings.J_bypass_voltage.c": 245.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 246.0, "general_inspection.readings.L_output_current.a": 1.4, "general_inspection.readings.L_output_current.b": 3.4, "general_inspection.readings.L_output_current.c": 2.5, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.8, "general_inspection.readings.M_active_power.c": 0.5, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.8, "general_inspection.readings.O_apparent_power.c": 0.6, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 11.0, "general_inspection.readings.P_output_power.c": 9.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": true, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All in good condition", "technician_name": "IZZUDIN", "technician_id": 22388, "supervisor_name": "MOHD IRZAN", "supervisor_id": 7094}
PS_PM_QTR_UPSSystem_4000673151.pdf | 4000673151 | {"station": "OCC", "date_time": "25/04/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 25.5, "general_inspection.readings.B_module_temperature.max": 27.0, "general_inspection.readings.C_battery_run_time": 173.0, "general_inspection.readings.D_output_frequency": 49.95, "general_inspection.readings.E_bypass_frequency": 49.96, "general_inspection.readings.F_battery_voltage_v.positive": 267.5, "general_inspection.readings.F_battery_voltage_v.negative": 267.5, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": null, "general_inspection.readings.I_rectifier_voltage.a": 246.7, "general_inspection.readings.I_rectifier_voltage.b": 245.8, "general_inspection.readings.I_rectifier_voltage.c": 245.4, "general_inspection.readings.J_bypass_voltage.a": 246.8, "general_inspection.readings.J_bypass_voltage.b": 246.0, "general_inspection.readings.J_bypass_voltage.c": 245.2, "general_inspection.readings.K_output_voltage.a": 230.0, "general_inspection.readings.K_output_voltage.b": 230.0, "general_inspection.readings.K_output_voltage.c": 230.0, "general_inspection.readings.L_output_current.a": 2.8, "general_inspection.readings.L_output_current.b": 4.2, "general_inspection.readings.L_output_current.c": 4.5, "general_inspection.readings.M_active_power.a": 0.5, "general_inspection.readings.M_active_power.b": 0.9, "general_inspection.readings.M_active_power.c": 0.9, "general_inspection.readings.N_reactive_power.a": 0.6, "general_inspection.readings.N_reactive_power.b": 1.0, "general_inspection.readings.N_reactive_power.c": 1.1, "general_inspection.readings.O_apparent_power.a": 2.5, "general_inspection.readings.O_apparent_power.b": 3.9, "general_inspection.readings.O_apparent_power.c": 4.0, "general_inspection.readings.P_output_power.a": 19.3, "general_inspection.readings.P_output_power.b": 29.0, "general_inspection.readings.P_output_power.c": 31.3, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": true, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": null, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "PM inspection already make by group Jurij and also tonight has test train so mainline remain ON.", "technician_name": "SUFFI SHUKHAIRI", "technician_id": 20971, "supervisor_name": "JURIS", "supervisor_id": 19924}
PS_PM_QTR_UPSSystem_4000673149.pdf | 4000673149 | {"station": "TSA", "date_time": "24/04/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 35.9, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 205.0, "general_inspection.readings.D_output_frequency": 49.99, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 226.0, "general_inspection.readings.F_battery_voltage_v.negative": 226.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 240.0, "general_inspection.readings.I_rectifier_voltage.b": 241.0, "general_inspection.readings.I_rectifier_voltage.c": 243.0, "general_inspection.readings.J_bypass_voltage.a": 241.0, "general_inspection.readings.J_bypass_voltage.b": 241.0, "general_inspection.readings.J_bypass_voltage.c": 243.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 1.5, "general_inspection.readings.L_output_current.b": 3.4, "general_inspection.readings.L_output_current.c": 3.7, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 1.2, "general_inspection.readings.M_active_power.c": 1.3, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.3, "general_inspection.readings.O_apparent_power.a": 0.0, "general_inspection.readings.O_apparent_power.b": 1.2, "general_inspection.readings.O_apparent_power.c": 1.4, "general_inspection.readings.P_output_power.a": 20.0, "general_inspection.readings.P_output_power.b": 20.0, "general_inspection.readings.P_output_power.c": 20.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": true, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All in good condition", "technician_name": "M.ISKANDAR", "technician_id": 20157, "supervisor_name": "NORIEZUWADI", "supervisor_id": 19234}
PS_PM_QTR_UPSSystem_4000672877.pdf | 4000672877 | {"station": "RAN", "date_time": "2025-04-20T00:00:00", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 32.1, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 238.0, "general_inspection.readings.D_output_frequency": 50.03, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 246.0, "general_inspection.readings.I_rectifier_voltage.b": 244.0, "general_inspection.readings.I_rectifier_voltage.c": 245.0, "general_inspection.readings.J_bypass_voltage.a": 244.0, "general_inspection.readings.J_bypass_voltage.b": 243.0, "general_inspection.readings.J_bypass_voltage.c": 246.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 2.2, "general_inspection.readings.L_output_current.b": 3.8, "general_inspection.readings.L_output_current.c": 4.9, "general_inspection.readings.M_active_power.a": 0.5, "general_inspection.readings.M_active_power.b": 0.8, "general_inspection.readings.M_active_power.c": 1.2, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.5, "general_inspection.readings.O_apparent_power.b": 1.0, "general_inspection.readings.O_apparent_power.c": 1.1, "general_inspection.readings.P_output_power.a": 7.0, "general_inspection.readings.P_output_power.b": 12.0, "general_inspection.readings.P_output_power.c": 17.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": true, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": null, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All in good condition", "technician_name": "IZZUDDIN", "technician_id": 22388, "supervisor_name": "MOHD IRZAN", "supervisor_id": 7094}
PS_PM_QTR_UPSSystem_4000673152.pdf | 4000673152 | {"station": "DCC", "date_time": "26/04/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 50.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 26.8, "general_inspection.readings.F_battery_voltage_v.negative": 26.8, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 242.0, "general_inspection.readings.I_rectifier_voltage.b": 242.0, "general_inspection.readings.I_rectifier_voltage.c": 245.0, "general_inspection.readings.J_bypass_voltage.a": 242.0, "general_inspection.readings.J_bypass_voltage.b": null, "general_inspection.readings.J_bypass_voltage.c": null, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": null, "general_inspection.readings.K_output_voltage.c": null, "general_inspection.readings.L_output_current.a": 38.8, "general_inspection.readings.L_output_current.b": null, "general_inspection.readings.L_output_current.c": null, "general_inspection.readings.M_active_power.a": null, "general_inspection.readings.M_active_power.b": null, "general_inspection.readings.M_active_power.c": null, "general_inspection.readings.N_reactive_power.a": 3.7, "general_inspection.readings.N_reactive_power.b": null, "general_inspection.readings.N_reactive_power.c": null, "general_inspection.readings.O_apparent_power.a": 8.9, "general_inspection.readings.O_apparent_power.b": null, "general_inspection.readings.O_apparent_power.c": null, "general_inspection.readings.P_output_power.a": null, "general_inspection.readings.P_output_power.b": null, "general_inspection.readings.P_output_power.c": null, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": true, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": null, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All in good condition", "technician_name": "SUFFI SHUKHAIRI", "technician_id": 20971, "supervisor_name": "AHMAD JURIS", "supervisor_id": 19924}
PS_PM_QTR_UPSSystem_4000672878.pdf | 4000672878 | {"station": "BAS", "date_time": "21/04/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": null, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 195.0, "general_inspection.readings.D_output_frequency": 49.99, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": null, "general_inspection.readings.F_battery_voltage_v.negative": null, "general_inspection.readings.G_battery_charge_car.positive": null, "general_inspection.readings.G_battery_charge_car.negative": null, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 246.0, "general_inspection.readings.I_rectifier_voltage.b": 246.0, "general_inspection.readings.I_rectifier_voltage.c": 248.0, "general_inspection.readings.J_bypass_voltage.a": 246.0, "general_inspection.readings.J_bypass_voltage.b": 240.0, "general_inspection.readings.J_bypass_voltage.c": 248.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.5, "general_inspection.readings.L_output_current.b": 3.5, "general_inspection.readings.L_output_current.c": 5.7, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.9, "general_inspection.readings.M_active_power.c": 1.4, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.8, "general_inspection.readings.O_apparent_power.c": 1.4, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 12.0, "general_inspection.readings.P_output_power.c": 0.1, "servicing_and_cleaning.set_maintenance_bypass_mode.status": null, "servicing_and_cleaning.switch_on_maintenance_bypass.status": null, "servicing_and_cleaning.confirm_display_panel.status": null, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": null, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": "", "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": null, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": null, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": null, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": null, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": null, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": null, "battery_backup_test.turn_off_main_switch_breaker.status": null, "battery_backup_test.confirm_alarm_sounding.status": null, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": null, "battery_backup_test.switch_on_back_main_switch_breaker.status": null, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All in good condition", "technician_name": " ", "technician_id": 20157, "supervisor_name": " ", "supervisor_id": 19234}
PS_PM_QTR_UPSSystem_4000672876.pdf | 4000672876 | {"station": "BNG", "date_time": "19/04/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 33.6, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 600.0, "general_inspection.readings.D_output_frequency": 50.04, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 243.0, "general_inspection.readings.I_rectifier_voltage.b": 243.0, "general_inspection.readings.I_rectifier_voltage.c": 246.0, "general_inspection.readings.J_bypass_voltage.a": 244.0, "general_inspection.readings.J_bypass_voltage.b": 243.0, "general_inspection.readings.J_bypass_voltage.c": 246.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 2.3, "general_inspection.readings.L_output_current.b": 6.2, "general_inspection.readings.L_output_current.c": 4.0, "general_inspection.readings.M_active_power.a": 0.5, "general_inspection.readings.M_active_power.b": 1.5, "general_inspection.readings.M_active_power.c": 0.3, "general_inspection.readings.N_reactive_power.a": 0.2, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 1.5, "general_inspection.readings.O_apparent_power.c": 0.3, "general_inspection.readings.P_output_power.a": 9.0, "general_inspection.readings.P_output_power.b": 25.0, "general_inspection.readings.P_output_power.c": 13.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": true, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": null, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": null, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All in good condition", "technician_name": "IZZUDDIN", "technician_id": 22388, "supervisor_name": "MOHD IRZAN", "supervisor_id": 7094}
PS_PM_QTR_UPSSystem_4000672879.pdf | 4000672879 | {"station": "CIT", "date_time": "2025-04-23T00:00:00", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": null, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 451.0, "general_inspection.readings.D_output_frequency": 49.98, "general_inspection.readings.E_bypass_frequency": 80.0, "general_inspection.readings.F_battery_voltage_v.positive": null, "general_inspection.readings.F_battery_voltage_v.negative": null, "general_inspection.readings.G_battery_charge_car.positive": null, "general_inspection.readings.G_battery_charge_car.negative": null, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 246.0, "general_inspection.readings.I_rectifier_voltage.b": 245.0, "general_inspection.readings.I_rectifier_voltage.c": 245.0, "general_inspection.readings.J_bypass_voltage.a": 246.0, "general_inspection.readings.J_bypass_voltage.b": 245.0, "general_inspection.readings.J_bypass_voltage.c": 245.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 0.8, "general_inspection.readings.L_output_current.b": 1.7, "general_inspection.readings.L_output_current.c": 2.2, "general_inspection.readings.M_active_power.a": 0.1, "general_inspection.readings.M_active_power.b": 0.3, "general_inspection.readings.M_active_power.c": 0.7, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.4, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.1, "general_inspection.readings.O_apparent_power.b": 0.4, "general_inspection.readings.O_apparent_power.c": 0.2, "general_inspection.readings.P_output_power.a": 0.0, "general_inspection.readings.P_output_power.b": 5.0, "general_inspection.readings.P_output_power.c": 11.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": null, "servicing_and_cleaning.switch_on_maintenance_bypass.status": null, "servicing_and_cleaning.confirm_display_panel.status": null, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": null, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": "", "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": null, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": null, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": null, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": null, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": null, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": null, "battery_backup_test.turn_off_main_switch_breaker.status": null, "battery_backup_test.confirm_alarm_sounding.status": null, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": null, "battery_backup_test.switch_on_back_main_switch_breaker.status": null, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All in good condition", "technician_name": "ISKANDAR", "technician_id": 20157, "supervisor_name": "NORIEZUWADI", "supervisor_id": 19234}
PS_PM_QTR_UPSSystem_4000673949.pdf | 4000673949 | {"station": "TUN", "date_time": "15/04/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": null, "general_inspection.readings.D_output_frequency": 50.01, "general_inspection.readings.E_bypass_frequency": 50.03, "general_inspection.readings.F_battery_voltage_v.positive": null, "general_inspection.readings.F_battery_voltage_v.negative": null, "general_inspection.readings.G_battery_charge_car.positive": null, "general_inspection.readings.G_battery_charge_car.negative": null, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 50.0, "general_inspection.readings.I_rectifier_voltage.b": 1.0, "general_inspection.readings.I_rectifier_voltage.c": 33.0, "general_inspection.readings.J_bypass_voltage.a": 240.0, "general_inspection.readings.J_bypass_voltage.b": 241.0, "general_inspection.readings.J_bypass_voltage.c": 243.0, "general_inspection.readings.K_output_voltage.a": 241.0, "general_inspection.readings.K_output_voltage.b": 241.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 0.2, "general_inspection.readings.L_output_current.b": 0.3, "general_inspection.readings.L_output_current.c": 1.9, "general_inspection.readings.M_active_power.a": 0.1, "general_inspection.readings.M_active_power.b": 0.4, "general_inspection.readings.M_active_power.c": 0.3, "general_inspection.readings.N_reactive_power.a": 0.5, "general_inspection.readings.N_reactive_power.b": 2.0, "general_inspection.readings.N_reactive_power.c": 1.5, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.0, "general_inspection.readings.O_apparent_power.c": 1.0, "general_inspection.readings.P_output_power.a": 8.3, "general_inspection.readings.P_output_power.b": 16.3, "general_inspection.readings.P_output_power.c": 15.4, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": true, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All in good condition", "technician_name": "IZUDDIN", "technician_id": 22388, "supervisor_name": "MOHD IRZAN", "supervisor_id": 7094}
PS_PM_QTR_UPSSystem_4000675828.pdf | 4000675828 | {"station": "KLS", "date_time": "14/04/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 34.6, "general_inspection.readings.B_module_temperature.max": 41.3, "general_inspection.readings.C_battery_run_time": 212.0, "general_inspection.readings.D_output_frequency": 49.98, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": null, "general_inspection.readings.F_battery_voltage_v.negative": null, "general_inspection.readings.G_battery_charge_car.positive": null, "general_inspection.readings.G_battery_charge_car.negative": null, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 257.0, "general_inspection.readings.I_rectifier_voltage.b": 256.0, "general_inspection.readings.I_rectifier_voltage.c": 258.0, "general_inspection.readings.J_bypass_voltage.a": 257.0, "general_inspection.readings.J_bypass_voltage.b": 256.0, "general_inspection.readings.J_bypass_voltage.c": 258.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 2.3, "general_inspection.readings.L_output_current.b": 4.6, "general_inspection.readings.L_output_current.c": 5.4, "general_inspection.readings.M_active_power.a": 0.5, "general_inspection.readings.M_active_power.b": 1.0, "general_inspection.readings.M_active_power.c": 1.3, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.4, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.5, "general_inspection.readings.O_apparent_power.b": 1.0, "general_inspection.readings.O_apparent_power.c": 1.3, "general_inspection.readings.P_output_power.a": 9.0, "general_inspection.readings.P_output_power.b": 14.0, "general_inspection.readings.P_output_power.c": 20.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": true, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All in goud Condition", "technician_name": "SHAHIN AMMAR", "technician_id": 20610, "supervisor_name": "DINESH", "supervisor_id": 7114}
PS_PM_QTR_UPSSystem_4000672875.pdf | 4000672875 | {"station": "IBI", "date_time": "18/04/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": null, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": null, "general_inspection.readings.A_battery_capacity": null, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": null, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": null, "general_inspection.readings.F_battery_voltage_v.negative": null, "general_inspection.readings.G_battery_charge_car.positive": null, "general_inspection.readings.G_battery_charge_car.negative": null, "general_inspection.readings.H_discharge_current": null, "general_inspection.readings.I_rectifier_voltage.a": null, "general_inspection.readings.I_rectifier_voltage.b": null, "general_inspection.readings.I_rectifier_voltage.c": null, "general_inspection.readings.J_bypass_voltage.a": null, "general_inspection.readings.J_bypass_voltage.b": null, "general_inspection.readings.J_bypass_voltage.c": null, "general_inspection.readings.K_output_voltage.a": null, "general_inspection.readings.K_output_voltage.b": null, "general_inspection.readings.K_output_voltage.c": null, "general_inspection.readings.L_output_current.a": null, "general_inspection.readings.L_output_current.b": null, "general_inspection.readings.L_output_current.c": null, "general_inspection.readings.M_active_power.a": null, "general_inspection.readings.M_active_power.b": null, "general_inspection.readings.M_active_power.c": null, "general_inspection.readings.N_reactive_power.a": null, "general_inspection.readings.N_reactive_power.b": null, "general_inspection.readings.N_reactive_power.c": null, "general_inspection.readings.O_apparent_power.a": null, "general_inspection.readings.O_apparent_power.b": null, "general_inspection.readings.O_apparent_power.c": null, "general_inspection.readings.P_output_power.a": null, "general_inspection.readings.P_output_power.b": null, "general_inspection.readings.P_output_power.c": null, "servicing_and_cleaning.set_maintenance_bypass_mode.status": null, "servicing_and_cleaning.switch_on_maintenance_bypass.status": null, "servicing_and_cleaning.confirm_display_panel.status": null, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": null, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": "", "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": null, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": true, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": null, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": null, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": null, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": null, "battery_backup_test.turn_off_main_switch_breaker.status": null, "battery_backup_test.confirm_alarm_sounding.status": null, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": null, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All in good conditon", "technician_name": "IZZUDDIN", "technician_id": 22388, "supervisor_name": "MOHD IRZAN", "supervisor_id": 7094}
SC_PM_NA_UPS_NA_1 (3).pdf |  | {"station": "OCC", "date_time": "27/10/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 26.6, "general_inspection.readings.B_module_temperature.max": 32.0, "general_inspection.readings.C_battery_run_time": 180.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": null, "general_inspection.readings.G_battery_charge_car.negative": null, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 247.0, "general_inspection.readings.I_rectifier_voltage.b": 247.0, "general_inspection.readings.I_rectifier_voltage.c": 247.0, "general_inspection.readings.J_bypass_voltage.a": 247.0, "general_inspection.readings.J_bypass_voltage.b": 247.0, "general_inspection.readings.J_bypass_voltage.c": 245.0, "general_inspection.readings.K_output_voltage.a": 230.0, "general_inspection.readings.K_output_voltage.b": 230.9, "general_inspection.readings.K_output_voltage.c": 230.0, "general_inspection.readings.L_output_current.a": null, "general_inspection.readings.L_output_current.b": 3.5, "general_inspection.readings.L_output_current.c": 4.3, "general_inspection.readings.M_active_power.a": 2.3, "general_inspection.readings.M_active_power.b": 2.9, "general_inspection.readings.M_active_power.c": 3.4, "general_inspection.readings.N_reactive_power.a": 6.6, "general_inspection.readings.N_reactive_power.b": 0.7, "general_inspection.readings.N_reactive_power.c": 1.0, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 0.7, "general_inspection.readings.O_apparent_power.c": 1.2, "general_inspection.readings.P_output_power.a": 0.03, "general_inspection.readings.P_output_power.b": 0.89, "general_inspection.readings.P_output_power.c": 0.84, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.3, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.3, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.4, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "UPS GOOD CONDITION", "technician_name": "", "technician_id": 7248, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_NA_UPS_NA_12.pdf |  | {"station": "OCC", "date_time": "27/07/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 629.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": null, "general_inspection.readings.G_battery_charge_car.negative": null, "general_inspection.readings.H_discharge_current": null, "general_inspection.readings.I_rectifier_voltage.a": 250.0, "general_inspection.readings.I_rectifier_voltage.b": 249.0, "general_inspection.readings.I_rectifier_voltage.c": 249.0, "general_inspection.readings.J_bypass_voltage.a": 251.0, "general_inspection.readings.J_bypass_voltage.b": 249.0, "general_inspection.readings.J_bypass_voltage.c": 248.0, "general_inspection.readings.K_output_voltage.a": 231.0, "general_inspection.readings.K_output_voltage.b": 231.0, "general_inspection.readings.K_output_voltage.c": 231.0, "general_inspection.readings.L_output_current.a": 13.0, "general_inspection.readings.L_output_current.b": 14.0, "general_inspection.readings.L_output_current.c": 17.0, "general_inspection.readings.M_active_power.a": 2.9, "general_inspection.readings.M_active_power.b": 3.0, "general_inspection.readings.M_active_power.c": 3.8, "general_inspection.readings.N_reactive_power.a": 1.1, "general_inspection.readings.N_reactive_power.b": 1.3, "general_inspection.readings.N_reactive_power.c": 1.7, "general_inspection.readings.O_apparent_power.a": 3.0, "general_inspection.readings.O_apparent_power.b": 3.4, "general_inspection.readings.O_apparent_power.c": 3.1, "general_inspection.readings.P_output_power.a": 23.0, "general_inspection.readings.P_output_power.b": 25.0, "general_inspection.readings.P_output_power.c": 31.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "Battery run test in good condition", "technician_name": "", "technician_id": 20826, "supervisor_name": "", "supervisor_id": 7110}
SC_PM_NA_UPS_NA_2 (2).pdf |  | {"station": "OCC", "date_time": "27/04/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 26.6, "general_inspection.readings.B_module_temperature.max": 32.0, "general_inspection.readings.C_battery_run_time": 180.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 247.0, "general_inspection.readings.I_rectifier_voltage.b": 247.0, "general_inspection.readings.I_rectifier_voltage.c": 247.0, "general_inspection.readings.J_bypass_voltage.a": 247.0, "general_inspection.readings.J_bypass_voltage.b": 247.0, "general_inspection.readings.J_bypass_voltage.c": 245.0, "general_inspection.readings.K_output_voltage.a": 230.0, "general_inspection.readings.K_output_voltage.b": 230.9, "general_inspection.readings.K_output_voltage.c": 230.0, "general_inspection.readings.L_output_current.a": 2.3, "general_inspection.readings.L_output_current.b": 3.5, "general_inspection.readings.L_output_current.c": 4.3, "general_inspection.readings.M_active_power.a": 2.3, "general_inspection.readings.M_active_power.b": 2.9, "general_inspection.readings.M_active_power.c": 3.4, "general_inspection.readings.N_reactive_power.a": 0.6, "general_inspection.readings.N_reactive_power.b": 0.7, "general_inspection.readings.N_reactive_power.c": 1.1, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 0.7, "general_inspection.readings.O_apparent_power.c": 1.2, "general_inspection.readings.P_output_power.a": 0.03, "general_inspection.readings.P_output_power.b": 0.89, "general_inspection.readings.P_output_power.c": 0.84, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.0, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.0, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.0, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 180.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 90.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 180.0, "comments_recommendation": "", "technician_name": "", "technician_id": 7248, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_NA_UPS_NA_3 (1).pdf |  | {"station": "DCC", "date_time": "26/07/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 28.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": null, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 272.0, "general_inspection.readings.F_battery_voltage_v.negative": 272.0, "general_inspection.readings.G_battery_charge_car.positive": null, "general_inspection.readings.G_battery_charge_car.negative": null, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 246.0, "general_inspection.readings.I_rectifier_voltage.b": 245.0, "general_inspection.readings.I_rectifier_voltage.c": 247.0, "general_inspection.readings.J_bypass_voltage.a": 246.0, "general_inspection.readings.J_bypass_voltage.b": 246.0, "general_inspection.readings.J_bypass_voltage.c": 246.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 37.7, "general_inspection.readings.L_output_current.b": 40.1, "general_inspection.readings.L_output_current.c": 36.7, "general_inspection.readings.M_active_power.a": 7.7, "general_inspection.readings.M_active_power.b": 7.6, "general_inspection.readings.M_active_power.c": 8.1, "general_inspection.readings.N_reactive_power.a": 8.7, "general_inspection.readings.N_reactive_power.b": 8.6, "general_inspection.readings.N_reactive_power.c": 8.8, "general_inspection.readings.O_apparent_power.a": 96.4, "general_inspection.readings.O_apparent_power.b": 98.6, "general_inspection.readings.O_apparent_power.c": 102.3, "general_inspection.readings.P_output_power.a": null, "general_inspection.readings.P_output_power.b": null, "general_inspection.readings.P_output_power.c": null, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": null, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": null, "battery_backup_test.turn_off_main_switch_breaker.status": null, "battery_backup_test.confirm_alarm_sounding.status": null, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": null, "battery_backup_test.switch_on_back_main_switch_breaker.status": null, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "Cannot do battery run test due to battery cannot support high load equipment.", "technician_name": "SYAZUAN", "technician_id": 19921, "supervisor_name": "MOHD RAZIF", "supervisor_id": 7222}
SC_PM_QTR_UPS_4000555059.pdf | 4000555059 | {"station": "DCC", "date_time": "26/10/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 28.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": null, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 272.0, "general_inspection.readings.F_battery_voltage_v.negative": 272.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": null, "general_inspection.readings.I_rectifier_voltage.a": null, "general_inspection.readings.I_rectifier_voltage.b": null, "general_inspection.readings.I_rectifier_voltage.c": null, "general_inspection.readings.J_bypass_voltage.a": 240.0, "general_inspection.readings.J_bypass_voltage.b": 242.0, "general_inspection.readings.J_bypass_voltage.c": 243.0, "general_inspection.readings.K_output_voltage.a": 243.0, "general_inspection.readings.K_output_voltage.b": 243.0, "general_inspection.readings.K_output_voltage.c": 243.0, "general_inspection.readings.L_output_current.a": 40.0, "general_inspection.readings.L_output_current.b": 39.0, "general_inspection.readings.L_output_current.c": 42.0, "general_inspection.readings.M_active_power.a": null, "general_inspection.readings.M_active_power.b": null, "general_inspection.readings.M_active_power.c": null, "general_inspection.readings.N_reactive_power.a": null, "general_inspection.readings.N_reactive_power.b": null, "general_inspection.readings.N_reactive_power.c": null, "general_inspection.readings.O_apparent_power.a": null, "general_inspection.readings.O_apparent_power.b": null, "general_inspection.readings.O_apparent_power.c": null, "general_inspection.readings.P_output_power.a": 5.7, "general_inspection.readings.P_output_power.b": 8.7, "general_inspection.readings.P_output_power.c": 8.7, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": null, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": null, "battery_backup_test.turn_off_main_switch_breaker.status": null, "battery_backup_test.confirm_alarm_sounding.status": null, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": null, "battery_backup_test.switch_on_back_main_switch_breaker.status": null, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "du not back up test, don't have spare batter, ups temporary in half condition, ups error battery faulty", "technician_name": "", "technician_id": 7248, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000493765.pdf | 4000493765 | {"station": "DCC", "date_time": "26/10/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 26.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": null, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 272.0, "general_inspection.readings.F_battery_voltage_v.negative": 272.0, "general_inspection.readings.G_battery_charge_car.positive": null, "general_inspection.readings.G_battery_charge_car.negative": null, "general_inspection.readings.H_discharge_current": null, "general_inspection.readings.I_rectifier_voltage.a": null, "general_inspection.readings.I_rectifier_voltage.b": null, "general_inspection.readings.I_rectifier_voltage.c": null, "general_inspection.readings.J_bypass_voltage.a": 240.0, "general_inspection.readings.J_bypass_voltage.b": 242.0, "general_inspection.readings.J_bypass_voltage.c": 243.0, "general_inspection.readings.K_output_voltage.a": 243.0, "general_inspection.readings.K_output_voltage.b": 243.0, "general_inspection.readings.K_output_voltage.c": 243.0, "general_inspection.readings.L_output_current.a": 40.0, "general_inspection.readings.L_output_current.b": 39.0, "general_inspection.readings.L_output_current.c": 42.0, "general_inspection.readings.M_active_power.a": null, "general_inspection.readings.M_active_power.b": null, "general_inspection.readings.M_active_power.c": null, "general_inspection.readings.N_reactive_power.a": null, "general_inspection.readings.N_reactive_power.b": null, "general_inspection.readings.N_reactive_power.c": null, "general_inspection.readings.O_apparent_power.a": null, "general_inspection.readings.O_apparent_power.b": null, "general_inspection.readings.O_apparent_power.c": null, "general_inspection.readings.P_output_power.a": 8.7, "general_inspection.readings.P_output_power.b": 8.7, "general_inspection.readings.P_output_power.c": null, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.2, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.8, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 20.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 20.0, "comments_recommendation": "all equipment in good conditions", "technician_name": "", "technician_id": 11727, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000597742_1.pdf | 4000597742 | {"station": "DCC", "date_time": "2024-01-26T00:00:00", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 28.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": null, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 272.0, "general_inspection.readings.F_battery_voltage_v.negative": 272.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": null, "general_inspection.readings.I_rectifier_voltage.a": null, "general_inspection.readings.I_rectifier_voltage.b": null, "general_inspection.readings.I_rectifier_voltage.c": null, "general_inspection.readings.J_bypass_voltage.a": 245.0, "general_inspection.readings.J_bypass_voltage.b": null, "general_inspection.readings.J_bypass_voltage.c": null, "general_inspection.readings.K_output_voltage.a": 228.0, "general_inspection.readings.K_output_voltage.b": null, "general_inspection.readings.K_output_voltage.c": null, "general_inspection.readings.L_output_current.a": 39.5, "general_inspection.readings.L_output_current.b": null, "general_inspection.readings.L_output_current.c": null, "general_inspection.readings.M_active_power.a": null, "general_inspection.readings.M_active_power.b": null, "general_inspection.readings.M_active_power.c": null, "general_inspection.readings.N_reactive_power.a": null, "general_inspection.readings.N_reactive_power.b": null, "general_inspection.readings.N_reactive_power.c": null, "general_inspection.readings.O_apparent_power.a": null, "general_inspection.readings.O_apparent_power.b": null, "general_inspection.readings.O_apparent_power.c": null, "general_inspection.readings.P_output_power.a": null, "general_inspection.readings.P_output_power.b": null, "general_inspection.readings.P_output_power.c": null, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": null, "servicing_and_cleaning.switch_off_all_battery_breakers.status": null, "servicing_and_cleaning.switch_off_both_of_module.status": null, "servicing_and_cleaning.open_screw_and_pull_both_module.status": null, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": null, "servicing_and_cleaning.normalized_all_battery_breakers.status": null, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": null, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": null, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": null, "battery_backup_test.confirm_alarm_sounding.status": null, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": null, "battery_backup_test.switch_on_back_main_switch_breaker.status": null, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "UPS in a good condition.\nI unit bateri voltage 25", "technician_name": "KARNA", "technician_id": " ", "supervisor_name": "AZHAR YUNUS", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000555059_1.pdf | 4000555059 | {"station": "DCC", "date_time": "26/07/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 28.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": null, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 272.0, "general_inspection.readings.F_battery_voltage_v.negative": 271.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": null, "general_inspection.readings.I_rectifier_voltage.a": null, "general_inspection.readings.I_rectifier_voltage.b": null, "general_inspection.readings.I_rectifier_voltage.c": null, "general_inspection.readings.J_bypass_voltage.a": 240.0, "general_inspection.readings.J_bypass_voltage.b": 242.0, "general_inspection.readings.J_bypass_voltage.c": 243.0, "general_inspection.readings.K_output_voltage.a": 243.0, "general_inspection.readings.K_output_voltage.b": 243.0, "general_inspection.readings.K_output_voltage.c": 243.0, "general_inspection.readings.L_output_current.a": 40.0, "general_inspection.readings.L_output_current.b": 39.0, "general_inspection.readings.L_output_current.c": 42.0, "general_inspection.readings.M_active_power.a": null, "general_inspection.readings.M_active_power.b": null, "general_inspection.readings.M_active_power.c": null, "general_inspection.readings.N_reactive_power.a": null, "general_inspection.readings.N_reactive_power.b": null, "general_inspection.readings.N_reactive_power.c": null, "general_inspection.readings.O_apparent_power.a": null, "general_inspection.readings.O_apparent_power.b": null, "general_inspection.readings.O_apparent_power.c": null, "general_inspection.readings.P_output_power.a": 5.7, "general_inspection.readings.P_output_power.b": 8.7, "general_inspection.readings.P_output_power.c": 8.7, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": null, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": null, "battery_backup_test.turn_off_main_switch_breaker.status": null, "battery_backup_test.confirm_alarm_sounding.status": null, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": null, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "UPS error battery faulty do not backup tes, ups temporary in half in dition, dant have spare battery.", "technician_name": "", "technician_id": 7110, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000480679.pdf | 4000480679 | {"station": "DCC", "date_time": "26/07/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 28.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": null, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 272.0, "general_inspection.readings.F_battery_voltage_v.negative": 272.0, "general_inspection.readings.G_battery_charge_car.positive": null, "general_inspection.readings.G_battery_charge_car.negative": null, "general_inspection.readings.H_discharge_current": null, "general_inspection.readings.I_rectifier_voltage.a": null, "general_inspection.readings.I_rectifier_voltage.b": null, "general_inspection.readings.I_rectifier_voltage.c": null, "general_inspection.readings.J_bypass_voltage.a": 242.0, "general_inspection.readings.J_bypass_voltage.b": null, "general_inspection.readings.J_bypass_voltage.c": null, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": null, "general_inspection.readings.K_output_voltage.c": null, "general_inspection.readings.L_output_current.a": 39.7, "general_inspection.readings.L_output_current.b": null, "general_inspection.readings.L_output_current.c": null, "general_inspection.readings.M_active_power.a": null, "general_inspection.readings.M_active_power.b": null, "general_inspection.readings.M_active_power.c": null, "general_inspection.readings.N_reactive_power.a": null, "general_inspection.readings.N_reactive_power.b": null, "general_inspection.readings.N_reactive_power.c": null, "general_inspection.readings.O_apparent_power.a": null, "general_inspection.readings.O_apparent_power.b": null, "general_inspection.readings.O_apparent_power.c": null, "general_inspection.readings.P_output_power.a": null, "general_inspection.readings.P_output_power.b": null, "general_inspection.readings.P_output_power.c": null, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.2, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.4, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 20.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 20.0, "comments_recommendation": "not display time estimate", "technician_name": " SYAHRUL AZWAN", "technician_id": 7110, "supervisor_name": "AZHAR YUNUS", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000608031.pdf | 4000608031 | {"station": "DCC", "date_time": "26/04/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 28.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": null, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 272.0, "general_inspection.readings.F_battery_voltage_v.negative": 272.0, "general_inspection.readings.G_battery_charge_car.positive": null, "general_inspection.readings.G_battery_charge_car.negative": null, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 246.0, "general_inspection.readings.I_rectifier_voltage.b": 245.0, "general_inspection.readings.I_rectifier_voltage.c": 247.0, "general_inspection.readings.J_bypass_voltage.a": 246.0, "general_inspection.readings.J_bypass_voltage.b": 246.0, "general_inspection.readings.J_bypass_voltage.c": 246.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 37.7, "general_inspection.readings.L_output_current.b": 40.1, "general_inspection.readings.L_output_current.c": 36.7, "general_inspection.readings.M_active_power.a": 7.7, "general_inspection.readings.M_active_power.b": 7.6, "general_inspection.readings.M_active_power.c": 8.1, "general_inspection.readings.N_reactive_power.a": 8.7, "general_inspection.readings.N_reactive_power.b": 8.6, "general_inspection.readings.N_reactive_power.c": 8.8, "general_inspection.readings.O_apparent_power.a": 96.4, "general_inspection.readings.O_apparent_power.b": 98.6, "general_inspection.readings.O_apparent_power.c": 102.3, "general_inspection.readings.P_output_power.a": null, "general_inspection.readings.P_output_power.b": null, "general_inspection.readings.P_output_power.c": null, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": null, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": null, "battery_backup_test.turn_off_main_switch_breaker.status": null, "battery_backup_test.confirm_alarm_sounding.status": null, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": null, "battery_backup_test.switch_on_back_main_switch_breaker.status": null, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "cant do battery run test because battery cannot support high load equipment", "technician_name": "", "technician_id": 21048, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000530701.pdf | 4000530701 | {"station": "OCC", "date_time": "26/04/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 28.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 180.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": null, "general_inspection.readings.I_rectifier_voltage.b": null, "general_inspection.readings.I_rectifier_voltage.c": null, "general_inspection.readings.J_bypass_voltage.a": 247.0, "general_inspection.readings.J_bypass_voltage.b": 247.0, "general_inspection.readings.J_bypass_voltage.c": 246.0, "general_inspection.readings.K_output_voltage.a": 230.0, "general_inspection.readings.K_output_voltage.b": 230.0, "general_inspection.readings.K_output_voltage.c": 230.0, "general_inspection.readings.L_output_current.a": 24.0, "general_inspection.readings.L_output_current.b": 29.0, "general_inspection.readings.L_output_current.c": 5.2, "general_inspection.readings.M_active_power.a": 0.5, "general_inspection.readings.M_active_power.b": 0.6, "general_inspection.readings.M_active_power.c": 1.1, "general_inspection.readings.N_reactive_power.a": 0.6, "general_inspection.readings.N_reactive_power.b": 0.7, "general_inspection.readings.N_reactive_power.c": 1.2, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 0.7, "general_inspection.readings.O_apparent_power.c": 1.2, "general_inspection.readings.P_output_power.a": 0.83, "general_inspection.readings.P_output_power.b": 0.89, "general_inspection.readings.P_output_power.c": 0.83, "servicing_and_cleaning.set_maintenance_bypass_mode.status": null, "servicing_and_cleaning.switch_on_maintenance_bypass.status": null, "servicing_and_cleaning.confirm_display_panel.status": null, "servicing_and_cleaning.switch_off_all_battery_breakers.status": null, "servicing_and_cleaning.switch_off_both_of_module.status": null, "servicing_and_cleaning.open_screw_and_pull_both_module.status": null, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.0, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.0, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.0, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 180.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 90.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 100.0, "comments_recommendation": "", "technician_name": "", "technician_id": 7222, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000467077.pdf | 4000467077 | {"station": "DCC", "date_time": "26/04/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 40.1, "general_inspection.readings.B_module_temperature.max": 38.8, "general_inspection.readings.C_battery_run_time": 349.0, "general_inspection.readings.D_output_frequency": 19.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 298.0, "general_inspection.readings.I_rectifier_voltage.b": 248.0, "general_inspection.readings.I_rectifier_voltage.c": 247.0, "general_inspection.readings.J_bypass_voltage.a": 230.0, "general_inspection.readings.J_bypass_voltage.b": 227.0, "general_inspection.readings.J_bypass_voltage.c": 277.0, "general_inspection.readings.K_output_voltage.a": 5.3, "general_inspection.readings.K_output_voltage.b": 5.5, "general_inspection.readings.K_output_voltage.c": 1.3, "general_inspection.readings.L_output_current.a": 1.2, "general_inspection.readings.L_output_current.b": 1.2, "general_inspection.readings.L_output_current.c": 2.3, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.1, "general_inspection.readings.M_active_power.c": 0.4, "general_inspection.readings.N_reactive_power.a": 0.3, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.4, "general_inspection.readings.O_apparent_power.a": 1.2, "general_inspection.readings.O_apparent_power.b": 1.2, "general_inspection.readings.O_apparent_power.c": 2.2, "general_inspection.readings.P_output_power.a": 19.0, "general_inspection.readings.P_output_power.b": 10.0, "general_inspection.readings.P_output_power.c": 37.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.6, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 15.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 15.0, "comments_recommendation": "not displaayed time astimate", "technician_name": "", "technician_id": 14952, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000669120.pdf | 4000669120 | {"station": "DCC", "date_time": "26/01/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 50.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 268.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 242.0, "general_inspection.readings.I_rectifier_voltage.b": 242.0, "general_inspection.readings.I_rectifier_voltage.c": 245.0, "general_inspection.readings.J_bypass_voltage.a": 242.0, "general_inspection.readings.J_bypass_voltage.b": null, "general_inspection.readings.J_bypass_voltage.c": null, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": null, "general_inspection.readings.K_output_voltage.c": null, "general_inspection.readings.L_output_current.a": 38.5, "general_inspection.readings.L_output_current.b": null, "general_inspection.readings.L_output_current.c": null, "general_inspection.readings.M_active_power.a": 8.6, "general_inspection.readings.M_active_power.b": null, "general_inspection.readings.M_active_power.c": null, "general_inspection.readings.N_reactive_power.a": 3.7, "general_inspection.readings.N_reactive_power.b": null, "general_inspection.readings.N_reactive_power.c": null, "general_inspection.readings.O_apparent_power.a": 8.9, "general_inspection.readings.O_apparent_power.b": null, "general_inspection.readings.O_apparent_power.c": null, "general_inspection.readings.P_output_power.a": null, "general_inspection.readings.P_output_power.b": null, "general_inspection.readings.P_output_power.c": null, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "", "technician_name": "", "technician_id": "", "supervisor_name": "", "supervisor_id": ""}
SC_PM_QTR_UPS_4000597742.pdf | 4000597742 | {"station": "DCC", "date_time": "26/01/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": null, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": null, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 272.0, "general_inspection.readings.F_battery_voltage_v.negative": 272.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": null, "general_inspection.readings.I_rectifier_voltage.a": null, "general_inspection.readings.I_rectifier_voltage.b": null, "general_inspection.readings.I_rectifier_voltage.c": null, "general_inspection.readings.J_bypass_voltage.a": 245.0, "general_inspection.readings.J_bypass_voltage.b": null, "general_inspection.readings.J_bypass_voltage.c": null, "general_inspection.readings.K_output_voltage.a": 238.0, "general_inspection.readings.K_output_voltage.b": null, "general_inspection.readings.K_output_voltage.c": null, "general_inspection.readings.L_output_current.a": null, "general_inspection.readings.L_output_current.b": null, "general_inspection.readings.L_output_current.c": null, "general_inspection.readings.M_active_power.a": null, "general_inspection.readings.M_active_power.b": null, "general_inspection.readings.M_active_power.c": null, "general_inspection.readings.N_reactive_power.a": null, "general_inspection.readings.N_reactive_power.b": null, "general_inspection.readings.N_reactive_power.c": null, "general_inspection.readings.O_apparent_power.a": null, "general_inspection.readings.O_apparent_power.b": null, "general_inspection.readings.O_apparent_power.c": null, "general_inspection.readings.P_output_power.a": null, "general_inspection.readings.P_output_power.b": null, "general_inspection.readings.P_output_power.c": null, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": null, "servicing_and_cleaning.confirm_display_panel.status": null, "servicing_and_cleaning.switch_off_all_battery_breakers.status": null, "servicing_and_cleaning.switch_off_both_of_module.status": null, "servicing_and_cleaning.open_screw_and_pull_both_module.status": null, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.5, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.8, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 25.0, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": null, "servicing_and_cleaning.normalized_all_battery_breakers.status": null, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": null, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": null, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": null, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": null, "battery_backup_test.confirm_alarm_sounding.status": null, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": null, "battery_backup_test.switch_on_back_main_switch_breaker.status": null, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "Ups in a good condition.\nI unit bateri voltage 25V", "technician_name": "", "technician_id": 7262, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000509113.pdf | 4000509113 | {"station": "OCC", "date_time": "26/01/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 28.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": null, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 272.0, "general_inspection.readings.F_battery_voltage_v.negative": 272.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": null, "general_inspection.readings.I_rectifier_voltage.a": null, "general_inspection.readings.I_rectifier_voltage.b": null, "general_inspection.readings.I_rectifier_voltage.c": null, "general_inspection.readings.J_bypass_voltage.a": 240.0, "general_inspection.readings.J_bypass_voltage.b": 242.0, "general_inspection.readings.J_bypass_voltage.c": 243.0, "general_inspection.readings.K_output_voltage.a": 243.0, "general_inspection.readings.K_output_voltage.b": 243.0, "general_inspection.readings.K_output_voltage.c": 243.0, "general_inspection.readings.L_output_current.a": 4.0, "general_inspection.readings.L_output_current.b": 3.9, "general_inspection.readings.L_output_current.c": 4.2, "general_inspection.readings.M_active_power.a": null, "general_inspection.readings.M_active_power.b": null, "general_inspection.readings.M_active_power.c": null, "general_inspection.readings.N_reactive_power.a": null, "general_inspection.readings.N_reactive_power.b": null, "general_inspection.readings.N_reactive_power.c": null, "general_inspection.readings.O_apparent_power.a": null, "general_inspection.readings.O_apparent_power.b": null, "general_inspection.readings.O_apparent_power.c": null, "general_inspection.readings.P_output_power.a": 5.7, "general_inspection.readings.P_output_power.b": 8.7, "general_inspection.readings.P_output_power.c": 8.7, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.9, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.9, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.8, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 20.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 20.0, "comments_recommendation": "Good Condition", "technician_name": "", "technician_id": 7223, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000446356.pdf | 4000446356 | {"station": "DCC", "date_time": "26/01/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 40.1, "general_inspection.readings.B_module_temperature.max": 38.8, "general_inspection.readings.C_battery_run_time": 349.0, "general_inspection.readings.D_output_frequency": 49.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 248.0, "general_inspection.readings.I_rectifier_voltage.b": 248.0, "general_inspection.readings.I_rectifier_voltage.c": 247.0, "general_inspection.readings.J_bypass_voltage.a": 249.0, "general_inspection.readings.J_bypass_voltage.b": 248.0, "general_inspection.readings.J_bypass_voltage.c": 248.0, "general_inspection.readings.K_output_voltage.a": 230.0, "general_inspection.readings.K_output_voltage.b": 238.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 5.3, "general_inspection.readings.L_output_current.b": 5.5, "general_inspection.readings.L_output_current.c": 10.7, "general_inspection.readings.M_active_power.a": 1.2, "general_inspection.readings.M_active_power.b": 1.2, "general_inspection.readings.M_active_power.c": 2.3, "general_inspection.readings.N_reactive_power.a": 0.3, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.4, "general_inspection.readings.O_apparent_power.a": 1.2, "general_inspection.readings.O_apparent_power.b": 1.2, "general_inspection.readings.O_apparent_power.c": 2.2, "general_inspection.readings.P_output_power.a": 19.0, "general_inspection.readings.P_output_power.b": 10.0, "general_inspection.readings.P_output_power.c": 35.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.6, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 15.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 15.0, "comments_recommendation": "equitment in good conditions but not view or display estimate time back up, -battery drain out very fast", "technician_name": "", "technician_id": "11727", "supervisor_name": "", "supervisor_id": "7111"}
SC_PM_QTR_UPS_4000647402.pdf | 4000647402 | {"station": "OCC", "date_time": "25/10/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 21.0, "general_inspection.readings.B_module_temperature.max": 23.3, "general_inspection.readings.C_battery_run_time": null, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.1, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": null, "general_inspection.readings.I_rectifier_voltage.a": 246.0, "general_inspection.readings.I_rectifier_voltage.b": 245.0, "general_inspection.readings.I_rectifier_voltage.c": 245.0, "general_inspection.readings.J_bypass_voltage.a": 247.0, "general_inspection.readings.J_bypass_voltage.b": 246.0, "general_inspection.readings.J_bypass_voltage.c": 244.0, "general_inspection.readings.K_output_voltage.a": 231.0, "general_inspection.readings.K_output_voltage.b": 231.0, "general_inspection.readings.K_output_voltage.c": 231.0, "general_inspection.readings.L_output_current.a": 11.0, "general_inspection.readings.L_output_current.b": 13.1, "general_inspection.readings.L_output_current.c": 19.3, "general_inspection.readings.M_active_power.a": 2.2, "general_inspection.readings.M_active_power.b": 2.7, "general_inspection.readings.M_active_power.c": 4.1, "general_inspection.readings.N_reactive_power.a": 2.5, "general_inspection.readings.N_reactive_power.b": 3.0, "general_inspection.readings.N_reactive_power.c": 4.5, "general_inspection.readings.O_apparent_power.a": 1.0, "general_inspection.readings.O_apparent_power.b": 1.1, "general_inspection.readings.O_apparent_power.c": 1.6, "general_inspection.readings.P_output_power.a": 18.5, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 34.1, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All battery in good condition:", "technician_name": "", "technician_id": 22153, "supervisor_name": "", "supervisor_id": 7222}
SC_PM_QTR_UPS_4000576167.pdf | 4000576167 | {"station": "OCC", "date_time": "25/10/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 26.6, "general_inspection.readings.B_module_temperature.max": 32.0, "general_inspection.readings.C_battery_run_time": 180.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 247.0, "general_inspection.readings.I_rectifier_voltage.b": 247.0, "general_inspection.readings.I_rectifier_voltage.c": 244.0, "general_inspection.readings.J_bypass_voltage.a": 247.0, "general_inspection.readings.J_bypass_voltage.b": 247.0, "general_inspection.readings.J_bypass_voltage.c": 245.0, "general_inspection.readings.K_output_voltage.a": 230.0, "general_inspection.readings.K_output_voltage.b": 230.9, "general_inspection.readings.K_output_voltage.c": 230.0, "general_inspection.readings.L_output_current.a": 2.8, "general_inspection.readings.L_output_current.b": 3.5, "general_inspection.readings.L_output_current.c": 4.3, "general_inspection.readings.M_active_power.a": 2.3, "general_inspection.readings.M_active_power.b": 2.9, "general_inspection.readings.M_active_power.c": 3.4, "general_inspection.readings.N_reactive_power.a": 0.6, "general_inspection.readings.N_reactive_power.b": 0.7, "general_inspection.readings.N_reactive_power.c": 1.1, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 0.7, "general_inspection.readings.O_apparent_power.c": 1.2, "general_inspection.readings.P_output_power.a": 0.03, "general_inspection.readings.P_output_power.b": 0.89, "general_inspection.readings.P_output_power.c": 0.84, "servicing_and_cleaning.set_maintenance_bypass_mode.status": null, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": null, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.5, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.3, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.4, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": null, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": null, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 195.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 15.0, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "ups good Condition", "technician_name": "", "technician_id": 7262, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000493787.pdf | 4000493787 | {"station": "OCC", "date_time": "25/10/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 32.5, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 180.0, "general_inspection.readings.D_output_frequency": 49.9, "general_inspection.readings.E_bypass_frequency": 49.97, "general_inspection.readings.F_battery_voltage_v.positive": 247.0, "general_inspection.readings.F_battery_voltage_v.negative": 247.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": null, "general_inspection.readings.I_rectifier_voltage.b": null, "general_inspection.readings.I_rectifier_voltage.c": null, "general_inspection.readings.J_bypass_voltage.a": 247.0, "general_inspection.readings.J_bypass_voltage.b": 246.0, "general_inspection.readings.J_bypass_voltage.c": 245.0, "general_inspection.readings.K_output_voltage.a": 230.0, "general_inspection.readings.K_output_voltage.b": 230.0, "general_inspection.readings.K_output_voltage.c": 230.0, "general_inspection.readings.L_output_current.a": 2.4, "general_inspection.readings.L_output_current.b": 3.1, "general_inspection.readings.L_output_current.c": 5.0, "general_inspection.readings.M_active_power.a": 0.5, "general_inspection.readings.M_active_power.b": 0.6, "general_inspection.readings.M_active_power.c": 0.2, "general_inspection.readings.N_reactive_power.a": 2.1, "general_inspection.readings.N_reactive_power.b": 2.8, "general_inspection.readings.N_reactive_power.c": 4.2, "general_inspection.readings.O_apparent_power.a": null, "general_inspection.readings.O_apparent_power.b": null, "general_inspection.readings.O_apparent_power.c": null, "general_inspection.readings.P_output_power.a": 0.8, "general_inspection.readings.P_output_power.b": 0.9, "general_inspection.readings.P_output_power.c": 0.9, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.8, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.0, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.8, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 180.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 90.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 180.0, "comments_recommendation": "all equipment in good conditions", "technician_name": "", "technician_id": 11727, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000615391.pdf | 4000615391 | {"station": "OCC", "date_time": "25/07/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 26.7, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 170.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 247.0, "general_inspection.readings.I_rectifier_voltage.b": 247.0, "general_inspection.readings.I_rectifier_voltage.c": 247.0, "general_inspection.readings.J_bypass_voltage.a": 246.0, "general_inspection.readings.J_bypass_voltage.b": 247.0, "general_inspection.readings.J_bypass_voltage.c": 246.0, "general_inspection.readings.K_output_voltage.a": 230.0, "general_inspection.readings.K_output_voltage.b": 230.0, "general_inspection.readings.K_output_voltage.c": 230.0, "general_inspection.readings.L_output_current.a": 2.3, "general_inspection.readings.L_output_current.b": 3.5, "general_inspection.readings.L_output_current.c": 4.3, "general_inspection.readings.M_active_power.a": 2.3, "general_inspection.readings.M_active_power.b": 2.9, "general_inspection.readings.M_active_power.c": 3.4, "general_inspection.readings.N_reactive_power.a": 0.6, "general_inspection.readings.N_reactive_power.b": 0.7, "general_inspection.readings.N_reactive_power.c": 1.1, "general_inspection.readings.O_apparent_power.a": 6.6, "general_inspection.readings.O_apparent_power.b": 0.7, "general_inspection.readings.O_apparent_power.c": 1.2, "general_inspection.readings.P_output_power.a": 0.03, "general_inspection.readings.P_output_power.b": 0.89, "general_inspection.readings.P_output_power.c": 0.85, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "ups In good condition", "technician_name": "", "technician_id": 22278, "supervisor_name": "", "supervisor_id": 7222}
SC_PM_QTR_UPS_4000555086.pdf | 4000555086 | {"station": "OCC", "date_time": "25/07/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 28.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 180.0, "general_inspection.readings.D_output_frequency": 80.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 347.0, "general_inspection.readings.I_rectifier_voltage.b": 247.0, "general_inspection.readings.I_rectifier_voltage.c": 244.0, "general_inspection.readings.J_bypass_voltage.a": 247.0, "general_inspection.readings.J_bypass_voltage.b": 247.0, "general_inspection.readings.J_bypass_voltage.c": 246.0, "general_inspection.readings.K_output_voltage.a": 230.0, "general_inspection.readings.K_output_voltage.b": 230.0, "general_inspection.readings.K_output_voltage.c": 230.0, "general_inspection.readings.L_output_current.a": 2.4, "general_inspection.readings.L_output_current.b": 2.9, "general_inspection.readings.L_output_current.c": 1.1, "general_inspection.readings.M_active_power.a": 0.6, "general_inspection.readings.M_active_power.b": 0.7, "general_inspection.readings.M_active_power.c": 1.2, "general_inspection.readings.N_reactive_power.a": 0.6, "general_inspection.readings.N_reactive_power.b": 0.7, "general_inspection.readings.N_reactive_power.c": 1.2, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 0.7, "general_inspection.readings.O_apparent_power.c": 1.2, "general_inspection.readings.P_output_power.a": 0.83, "general_inspection.readings.P_output_power.b": 0.84, "general_inspection.readings.P_output_power.c": 0.83, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "- ups in good condition", "technician_name": "", "technician_id": 7110, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000608059.pdf | 4000608059 | {"station": "OCC", "date_time": "25/04/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 629.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": null, "general_inspection.readings.G_battery_charge_car.negative": null, "general_inspection.readings.H_discharge_current": null, "general_inspection.readings.I_rectifier_voltage.a": 250.0, "general_inspection.readings.I_rectifier_voltage.b": 249.0, "general_inspection.readings.I_rectifier_voltage.c": 249.0, "general_inspection.readings.J_bypass_voltage.a": 251.0, "general_inspection.readings.J_bypass_voltage.b": 249.0, "general_inspection.readings.J_bypass_voltage.c": 248.0, "general_inspection.readings.K_output_voltage.a": 231.0, "general_inspection.readings.K_output_voltage.b": 231.0, "general_inspection.readings.K_output_voltage.c": 231.0, "general_inspection.readings.L_output_current.a": 13.0, "general_inspection.readings.L_output_current.b": 14.0, "general_inspection.readings.L_output_current.c": 17.0, "general_inspection.readings.M_active_power.a": 2.9, "general_inspection.readings.M_active_power.b": 3.0, "general_inspection.readings.M_active_power.c": 3.8, "general_inspection.readings.N_reactive_power.a": 1.1, "general_inspection.readings.N_reactive_power.b": 1.3, "general_inspection.readings.N_reactive_power.c": 1.7, "general_inspection.readings.O_apparent_power.a": 3.0, "general_inspection.readings.O_apparent_power.b": 3.4, "general_inspection.readings.O_apparent_power.c": 3.1, "general_inspection.readings.P_output_power.a": 23.0, "general_inspection.readings.P_output_power.b": 25.0, "general_inspection.readings.P_output_power.c": 31.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "Battery run test in good condition.", "technician_name": "", "technician_id": 21048, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000530675.pdf | 4000530675 | {"station": "DCC", "date_time": "25/04/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 28.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": null, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 272.0, "general_inspection.readings.F_battery_voltage_v.negative": 272.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": null, "general_inspection.readings.I_rectifier_voltage.a": null, "general_inspection.readings.I_rectifier_voltage.b": null, "general_inspection.readings.I_rectifier_voltage.c": null, "general_inspection.readings.J_bypass_voltage.a": 240.0, "general_inspection.readings.J_bypass_voltage.b": 242.0, "general_inspection.readings.J_bypass_voltage.c": 243.0, "general_inspection.readings.K_output_voltage.a": 243.0, "general_inspection.readings.K_output_voltage.b": 243.0, "general_inspection.readings.K_output_voltage.c": 243.0, "general_inspection.readings.L_output_current.a": 40.0, "general_inspection.readings.L_output_current.b": 39.0, "general_inspection.readings.L_output_current.c": 42.0, "general_inspection.readings.M_active_power.a": null, "general_inspection.readings.M_active_power.b": null, "general_inspection.readings.M_active_power.c": null, "general_inspection.readings.N_reactive_power.a": null, "general_inspection.readings.N_reactive_power.b": null, "general_inspection.readings.N_reactive_power.c": null, "general_inspection.readings.O_apparent_power.a": null, "general_inspection.readings.O_apparent_power.b": null, "general_inspection.readings.O_apparent_power.c": null, "general_inspection.readings.P_output_power.a": 7.7, "general_inspection.readings.P_output_power.b": 8.7, "general_inspection.readings.P_output_power.c": 8.7, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.9, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.7, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.8, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 20.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 20.0, "comments_recommendation": "", "technician_name": "", "technician_id": 7222, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000467097.pdf | 4000467097 | {"station": "OCC", "date_time": "25/04/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 24.7, "general_inspection.readings.B_module_temperature.max": 22.6, "general_inspection.readings.C_battery_run_time": 153.0, "general_inspection.readings.D_output_frequency": 49.9, "general_inspection.readings.E_bypass_frequency": 49.6, "general_inspection.readings.F_battery_voltage_v.positive": 261.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 268.0, "general_inspection.readings.G_battery_charge_car.negative": 288.0, "general_inspection.readings.H_discharge_current": 1.3, "general_inspection.readings.I_rectifier_voltage.a": null, "general_inspection.readings.I_rectifier_voltage.b": null, "general_inspection.readings.I_rectifier_voltage.c": null, "general_inspection.readings.J_bypass_voltage.a": 244.0, "general_inspection.readings.J_bypass_voltage.b": 243.0, "general_inspection.readings.J_bypass_voltage.c": 243.0, "general_inspection.readings.K_output_voltage.a": 241.0, "general_inspection.readings.K_output_voltage.b": 241.0, "general_inspection.readings.K_output_voltage.c": 214.0, "general_inspection.readings.L_output_current.a": 0.2, "general_inspection.readings.L_output_current.b": 2.1, "general_inspection.readings.L_output_current.c": 2.8, "general_inspection.readings.M_active_power.a": 0.4, "general_inspection.readings.M_active_power.b": 0.2, "general_inspection.readings.M_active_power.c": 2.4, "general_inspection.readings.N_reactive_power.a": 0.5, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.5, "general_inspection.readings.O_apparent_power.a": 0.5, "general_inspection.readings.O_apparent_power.b": 1.4, "general_inspection.readings.O_apparent_power.c": 2.6, "general_inspection.readings.P_output_power.a": 7.0, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 36.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.4, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 20.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 50.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 20.0, "comments_recommendation": "ok", "technician_name": "", "technician_id": 14952, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000509061.pdf | 4000509061 | {"station": "OCC", "date_time": "25/01/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 28.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 180.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": null, "general_inspection.readings.I_rectifier_voltage.b": null, "general_inspection.readings.I_rectifier_voltage.c": null, "general_inspection.readings.J_bypass_voltage.a": 247.0, "general_inspection.readings.J_bypass_voltage.b": 247.0, "general_inspection.readings.J_bypass_voltage.c": 246.0, "general_inspection.readings.K_output_voltage.a": 230.0, "general_inspection.readings.K_output_voltage.b": 230.0, "general_inspection.readings.K_output_voltage.c": 230.0, "general_inspection.readings.L_output_current.a": 24.0, "general_inspection.readings.L_output_current.b": 29.0, "general_inspection.readings.L_output_current.c": 5.2, "general_inspection.readings.M_active_power.a": 0.5, "general_inspection.readings.M_active_power.b": 0.6, "general_inspection.readings.M_active_power.c": 1.2, "general_inspection.readings.N_reactive_power.a": 0.6, "general_inspection.readings.N_reactive_power.b": 0.7, "general_inspection.readings.N_reactive_power.c": 1.2, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 0.7, "general_inspection.readings.O_apparent_power.c": 1.2, "general_inspection.readings.P_output_power.a": 0.83, "general_inspection.readings.P_output_power.b": 0.89, "general_inspection.readings.P_output_power.c": 0.93, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.0, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.0, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.0, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 180.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 90.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 180.0, "comments_recommendation": "GOOD CONDITION", "technician_name": "", "technician_id": 7223, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000446335.pdf | 4000446335 | {"station": "OCC", "date_time": "25/01/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 48.1, "general_inspection.readings.B_module_temperature.max": 37.8, "general_inspection.readings.C_battery_run_time": 270.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 49.9, "general_inspection.readings.F_battery_voltage_v.positive": 207.0, "general_inspection.readings.F_battery_voltage_v.negative": 240.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 248.0, "general_inspection.readings.I_rectifier_voltage.b": 248.0, "general_inspection.readings.I_rectifier_voltage.c": 248.0, "general_inspection.readings.J_bypass_voltage.a": 249.0, "general_inspection.readings.J_bypass_voltage.b": 249.0, "general_inspection.readings.J_bypass_voltage.c": 239.0, "general_inspection.readings.K_output_voltage.a": 238.0, "general_inspection.readings.K_output_voltage.b": 238.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 5.3, "general_inspection.readings.L_output_current.b": 5.3, "general_inspection.readings.L_output_current.c": 10.2, "general_inspection.readings.M_active_power.a": 1.2, "general_inspection.readings.M_active_power.b": 1.2, "general_inspection.readings.M_active_power.c": 2.3, "general_inspection.readings.N_reactive_power.a": 0.3, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.4, "general_inspection.readings.O_apparent_power.a": 1.2, "general_inspection.readings.O_apparent_power.b": 1.2, "general_inspection.readings.O_apparent_power.c": 2.5, "general_inspection.readings.P_output_power.a": 14.0, "general_inspection.readings.P_output_power.b": 18.0, "general_inspection.readings.P_output_power.c": 36.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.6, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 180.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 90.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 80.0, "comments_recommendation": "all equitment in good conditions", "technician_name": "", "technician_id": 11727, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000480717.pdf | 4000480717 | {"station": "TSA", "date_time": "24/04/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 42.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 185.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 212.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 238.0, "general_inspection.readings.I_rectifier_voltage.b": 237.0, "general_inspection.readings.I_rectifier_voltage.c": 240.0, "general_inspection.readings.J_bypass_voltage.a": 238.0, "general_inspection.readings.J_bypass_voltage.b": 239.0, "general_inspection.readings.J_bypass_voltage.c": 240.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 241.0, "general_inspection.readings.K_output_voltage.c": 244.0, "general_inspection.readings.L_output_current.a": 1.6, "general_inspection.readings.L_output_current.b": 1.5, "general_inspection.readings.L_output_current.c": 4.4, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 1.2, "general_inspection.readings.M_active_power.c": 1.0, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.4, "general_inspection.readings.O_apparent_power.b": 1.3, "general_inspection.readings.O_apparent_power.c": 1.0, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 17.0, "general_inspection.readings.P_output_power.c": 15.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.6, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 180.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 90.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 90.0, "comments_recommendation": "ok.", "technician_name": "MOHD RAZIF", "technician_id": 7222, "supervisor_name": "AZHAR YUNUS", "supervisor_id": 7111}
SC_PM_NA_UPS_NA (7).pdf |  | {"station": "TSA", "date_time": "24/10/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 27.8, "general_inspection.readings.B_module_temperature.max": 28.9, "general_inspection.readings.C_battery_run_time": 210.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 241.0, "general_inspection.readings.I_rectifier_voltage.b": 240.0, "general_inspection.readings.I_rectifier_voltage.c": 243.0, "general_inspection.readings.J_bypass_voltage.a": 241.0, "general_inspection.readings.J_bypass_voltage.b": 240.0, "general_inspection.readings.J_bypass_voltage.c": 242.0, "general_inspection.readings.K_output_voltage.a": null, "general_inspection.readings.K_output_voltage.b": null, "general_inspection.readings.K_output_voltage.c": null, "general_inspection.readings.L_output_current.a": 1.4, "general_inspection.readings.L_output_current.b": 5.3, "general_inspection.readings.L_output_current.c": 6.0, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 1.1, "general_inspection.readings.M_active_power.c": 1.3, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.4, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.1, "general_inspection.readings.O_apparent_power.c": 1.4, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 20.0, "general_inspection.readings.P_output_power.c": 21.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All equipment are in good condition.", "technician_name": "", "technician_id": 20005, "supervisor_name": "", "supervisor_id": 7248}
SC_PM_QTR_UPS_4000576188.pdf | 4000576188 | {"station": "TSA", "date_time": "24/10/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 33.0, "general_inspection.readings.B_module_temperature.max": 39.1, "general_inspection.readings.C_battery_run_time": 228.0, "general_inspection.readings.D_output_frequency": 50.04, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 234.0, "general_inspection.readings.I_rectifier_voltage.b": 236.0, "general_inspection.readings.I_rectifier_voltage.c": 237.0, "general_inspection.readings.J_bypass_voltage.a": 234.0, "general_inspection.readings.J_bypass_voltage.b": 236.0, "general_inspection.readings.J_bypass_voltage.c": 237.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.2, "general_inspection.readings.L_output_current.b": 4.2, "general_inspection.readings.L_output_current.c": 5.4, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 1.0, "general_inspection.readings.M_active_power.c": 1.2, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.3, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.0, "general_inspection.readings.O_apparent_power.c": 1.2, "general_inspection.readings.P_output_power.a": 4.0, "general_inspection.readings.P_output_power.b": 14.0, "general_inspection.readings.P_output_power.c": 20.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": 228.0, "comments_recommendation": "All Good Condition", "technician_name": "", "technician_id": 7262, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000509052.pdf | 4000509052 | {"station": "TSA", "date_time": "24/10/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 28.0, "general_inspection.readings.B_module_temperature.max": 33.0, "general_inspection.readings.C_battery_run_time": 207.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 237.0, "general_inspection.readings.I_rectifier_voltage.b": 238.0, "general_inspection.readings.I_rectifier_voltage.c": 240.0, "general_inspection.readings.J_bypass_voltage.a": 237.0, "general_inspection.readings.J_bypass_voltage.b": 238.0, "general_inspection.readings.J_bypass_voltage.c": 240.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.0, "general_inspection.readings.L_output_current.b": 4.8, "general_inspection.readings.L_output_current.c": 6.2, "general_inspection.readings.M_active_power.a": 0.2, "general_inspection.readings.M_active_power.b": 1.3, "general_inspection.readings.M_active_power.c": 1.4, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.3, "general_inspection.readings.O_apparent_power.a": 0.2, "general_inspection.readings.O_apparent_power.b": 1.2, "general_inspection.readings.O_apparent_power.c": 1.4, "general_inspection.readings.P_output_power.a": 3.0, "general_inspection.readings.P_output_power.b": 19.0, "general_inspection.readings.P_output_power.c": 21.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.5, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.8, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.8, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 180.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 90.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 180.0, "comments_recommendation": "2 batery faulty and all equipment in good conditions", "technician_name": "", "technician_id": "11727", "supervisor_name": "", "supervisor_id": "7111"}
SC_PM_NA_UPS_NA_9.pdf |  | {"station": "TSA", "date_time": "24/07/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 33.7, "general_inspection.readings.B_module_temperature.max": 40.2, "general_inspection.readings.C_battery_run_time": 210.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 237.0, "general_inspection.readings.I_rectifier_voltage.b": 239.0, "general_inspection.readings.I_rectifier_voltage.c": 240.0, "general_inspection.readings.J_bypass_voltage.a": 237.0, "general_inspection.readings.J_bypass_voltage.b": 239.0, "general_inspection.readings.J_bypass_voltage.c": 24.0, "general_inspection.readings.K_output_voltage.a": null, "general_inspection.readings.K_output_voltage.b": null, "general_inspection.readings.K_output_voltage.c": null, "general_inspection.readings.L_output_current.a": 1.3, "general_inspection.readings.L_output_current.b": 4.5, "general_inspection.readings.L_output_current.c": 5.6, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 1.1, "general_inspection.readings.M_active_power.c": 1.3, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.3, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.1, "general_inspection.readings.O_apparent_power.c": 1.3, "general_inspection.readings.P_output_power.a": 4.0, "general_inspection.readings.P_output_power.b": 17.0, "general_inspection.readings.P_output_power.c": 20.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 53.7, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 53.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 53.6, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "Battery & Module in good condition.", "technician_name": "", "technician_id": "19921", "supervisor_name": "", "supervisor_id": 7222}
SC_PM_QTR_UPS_4000555036.pdf | 4000555036 | {"station": "BAS", "date_time": "24/07/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 31.5, "general_inspection.readings.B_module_temperature.max": 38.4, "general_inspection.readings.C_battery_run_time": 225.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 249.0, "general_inspection.readings.I_rectifier_voltage.b": 249.0, "general_inspection.readings.I_rectifier_voltage.c": 249.0, "general_inspection.readings.J_bypass_voltage.a": 249.0, "general_inspection.readings.J_bypass_voltage.b": 249.0, "general_inspection.readings.J_bypass_voltage.c": 260.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.5, "general_inspection.readings.L_output_current.b": 3.8, "general_inspection.readings.L_output_current.c": 6.0, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.8, "general_inspection.readings.M_active_power.c": 1.4, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 1.3, "general_inspection.readings.O_apparent_power.b": 0.8, "general_inspection.readings.O_apparent_power.c": 1.4, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 12.0, "general_inspection.readings.P_output_power.c": 32.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "", "technician_name": "", "technician_id": 7222, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000555099.pdf | 4000555099 | {"station": "TSA", "date_time": "24/07/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 32.7, "general_inspection.readings.B_module_temperature.max": 39.3, "general_inspection.readings.C_battery_run_time": 235.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 206.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 235.0, "general_inspection.readings.I_rectifier_voltage.b": 236.0, "general_inspection.readings.I_rectifier_voltage.c": 237.0, "general_inspection.readings.J_bypass_voltage.a": 240.0, "general_inspection.readings.J_bypass_voltage.b": 239.0, "general_inspection.readings.J_bypass_voltage.c": 240.0, "general_inspection.readings.K_output_voltage.a": 1.4, "general_inspection.readings.K_output_voltage.b": 4.8, "general_inspection.readings.K_output_voltage.c": 5.1, "general_inspection.readings.L_output_current.a": 0.3, "general_inspection.readings.L_output_current.b": 1.0, "general_inspection.readings.L_output_current.c": 1.2, "general_inspection.readings.M_active_power.a": 0.0, "general_inspection.readings.M_active_power.b": 0.1, "general_inspection.readings.M_active_power.c": 0.3, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.3, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.0, "general_inspection.readings.O_apparent_power.c": 1.2, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 15.0, "general_inspection.readings.P_output_power.c": 18.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All batery in good condition.\n connection cable and inficator module good condition", "technician_name": "", "technician_id": 7110, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000480715.pdf | 4000480715 | {"station": "TSA", "date_time": "24/07/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 33.9, "general_inspection.readings.B_module_temperature.max": 40.5, "general_inspection.readings.C_battery_run_time": 290.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 240.0, "general_inspection.readings.I_rectifier_voltage.b": 241.0, "general_inspection.readings.I_rectifier_voltage.c": 243.0, "general_inspection.readings.J_bypass_voltage.a": 240.0, "general_inspection.readings.J_bypass_voltage.b": 241.0, "general_inspection.readings.J_bypass_voltage.c": 242.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.0, "general_inspection.readings.L_output_current.b": 4.1, "general_inspection.readings.L_output_current.c": 4.9, "general_inspection.readings.M_active_power.a": 0.2, "general_inspection.readings.M_active_power.b": 1.0, "general_inspection.readings.M_active_power.c": 1.1, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.2, "general_inspection.readings.O_apparent_power.b": 1.0, "general_inspection.readings.O_apparent_power.c": 1.2, "general_inspection.readings.P_output_power.a": 4.0, "general_inspection.readings.P_output_power.b": 16.0, "general_inspection.readings.P_output_power.c": 17.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.3, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.4, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 540.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "ups faulty\\alarm battery discharge appear\\must battery broken\temporary maintanance bypass", "technician_name": "SYAHRUL AZWAN", "technician_id": 7110, "supervisor_name": "AZHAR YUNUS", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000608074.pdf | 4000608074 | {"station": "TSA", "date_time": "2024-04-24T00:00:00", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": null, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 33.7, "general_inspection.readings.B_module_temperature.max": 40.1, "general_inspection.readings.C_battery_run_time": 218.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 236.0, "general_inspection.readings.I_rectifier_voltage.b": 239.0, "general_inspection.readings.I_rectifier_voltage.c": 241.0, "general_inspection.readings.J_bypass_voltage.a": 236.0, "general_inspection.readings.J_bypass_voltage.b": 239.0, "general_inspection.readings.J_bypass_voltage.c": 241.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.6, "general_inspection.readings.L_output_current.b": 5.5, "general_inspection.readings.L_output_current.c": 6.1, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 1.3, "general_inspection.readings.M_active_power.c": 1.3, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.3, "general_inspection.readings.O_apparent_power.a": 0.4, "general_inspection.readings.O_apparent_power.b": 1.2, "general_inspection.readings.O_apparent_power.c": 1.3, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 20.0, "general_inspection.readings.P_output_power.c": 21.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "-Hardware In good condition", "technician_name": "", "technician_id": 20079, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000530710.pdf | 4000530710 | {"station": "TSA", "date_time": "24/04/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 28.0, "general_inspection.readings.B_module_temperature.max": 33.0, "general_inspection.readings.C_battery_run_time": 196.2, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.6, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 237.0, "general_inspection.readings.I_rectifier_voltage.b": 238.0, "general_inspection.readings.I_rectifier_voltage.c": 240.0, "general_inspection.readings.J_bypass_voltage.a": 237.0, "general_inspection.readings.J_bypass_voltage.b": 238.0, "general_inspection.readings.J_bypass_voltage.c": 260.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 259.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.0, "general_inspection.readings.L_output_current.b": 4.8, "general_inspection.readings.L_output_current.c": 6.2, "general_inspection.readings.M_active_power.a": 0.2, "general_inspection.readings.M_active_power.b": 1.2, "general_inspection.readings.M_active_power.c": 1.7, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.3, "general_inspection.readings.O_apparent_power.a": 0.2, "general_inspection.readings.O_apparent_power.b": 1.2, "general_inspection.readings.O_apparent_power.c": 1.4, "general_inspection.readings.P_output_power.a": 3.0, "general_inspection.readings.P_output_power.b": 19.0, "general_inspection.readings.P_output_power.c": 21.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.5, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.7, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 180.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 90.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 180.0, "comments_recommendation": "good Condition", "technician_name": "", "technician_id": 7110, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000668040.pdf | 4000668040 | {"station": "TSA", "date_time": "24/01/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 29.9, "general_inspection.readings.B_module_temperature.max": 35.9, "general_inspection.readings.C_battery_run_time": 204.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 239.0, "general_inspection.readings.I_rectifier_voltage.b": 241.0, "general_inspection.readings.I_rectifier_voltage.c": 243.0, "general_inspection.readings.J_bypass_voltage.a": 240.0, "general_inspection.readings.J_bypass_voltage.b": 241.0, "general_inspection.readings.J_bypass_voltage.c": 243.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 1.5, "general_inspection.readings.L_output_current.b": 5.5, "general_inspection.readings.L_output_current.c": 6.2, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 1.2, "general_inspection.readings.M_active_power.c": 1.4, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.4, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.1, "general_inspection.readings.O_apparent_power.c": 1.4, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 20.0, "general_inspection.readings.P_output_power.c": 21.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "UPS IN GOOD CONDITION", "technician_name": "", "technician_id": 22876, "supervisor_name": "", "supervisor_id": 7110}
SC_PM_QTR_UPS_4000597870.pdf | 4000597870 | {"station": "TSA", "date_time": "24/01/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 33.0, "general_inspection.readings.B_module_temperature.max": 39.1, "general_inspection.readings.C_battery_run_time": 228.0, "general_inspection.readings.D_output_frequency": 50.04, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 234.0, "general_inspection.readings.I_rectifier_voltage.b": 236.0, "general_inspection.readings.I_rectifier_voltage.c": 237.0, "general_inspection.readings.J_bypass_voltage.a": 234.0, "general_inspection.readings.J_bypass_voltage.b": 236.0, "general_inspection.readings.J_bypass_voltage.c": 237.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.2, "general_inspection.readings.L_output_current.b": 4.3, "general_inspection.readings.L_output_current.c": 5.4, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 1.0, "general_inspection.readings.M_active_power.c": 1.2, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.3, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.0, "general_inspection.readings.O_apparent_power.c": 1.2, "general_inspection.readings.P_output_power.a": 4.0, "general_inspection.readings.P_output_power.b": 14.0, "general_inspection.readings.P_output_power.c": 20.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All good condition", "technician_name": "", "technician_id": 7248, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000509053.pdf | 4000509053 | {"station": "TSA", "date_time": "24/01/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 28.0, "general_inspection.readings.B_module_temperature.max": 33.0, "general_inspection.readings.C_battery_run_time": 207.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 237.0, "general_inspection.readings.I_rectifier_voltage.b": 238.0, "general_inspection.readings.I_rectifier_voltage.c": 240.0, "general_inspection.readings.J_bypass_voltage.a": 237.0, "general_inspection.readings.J_bypass_voltage.b": 238.0, "general_inspection.readings.J_bypass_voltage.c": 240.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.07, "general_inspection.readings.L_output_current.b": 48.0, "general_inspection.readings.L_output_current.c": 6.2, "general_inspection.readings.M_active_power.a": 0.2, "general_inspection.readings.M_active_power.b": 1.3, "general_inspection.readings.M_active_power.c": 1.4, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.3, "general_inspection.readings.O_apparent_power.a": 0.2, "general_inspection.readings.O_apparent_power.b": 1.2, "general_inspection.readings.O_apparent_power.c": 1.4, "general_inspection.readings.P_output_power.a": 3.0, "general_inspection.readings.P_output_power.b": 19.0, "general_inspection.readings.P_output_power.c": 21.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.5, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.7, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.7, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 180.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 90.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 180.0, "comments_recommendation": "Good Condition", "technician_name": "", "technician_id": 7223, "supervisor_name": "", "supervisor_id": "7111"}
SC_PM_QTR_UPS_4000446312.pdf | 4000446312 | {"station": "TSA", "date_time": "24/01/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 42.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 185.0, "general_inspection.readings.D_output_frequency": 30.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 272.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 238.0, "general_inspection.readings.I_rectifier_voltage.b": 237.0, "general_inspection.readings.I_rectifier_voltage.c": 240.0, "general_inspection.readings.J_bypass_voltage.a": 238.0, "general_inspection.readings.J_bypass_voltage.b": 239.0, "general_inspection.readings.J_bypass_voltage.c": 240.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 241.0, "general_inspection.readings.K_output_voltage.c": 244.0, "general_inspection.readings.L_output_current.a": 1.6, "general_inspection.readings.L_output_current.b": 1.3, "general_inspection.readings.L_output_current.c": 4.4, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 1.2, "general_inspection.readings.M_active_power.c": 1.0, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.4, "general_inspection.readings.O_apparent_power.b": 1.3, "general_inspection.readings.O_apparent_power.c": 1.0, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 17.0, "general_inspection.readings.P_output_power.c": 15.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.6, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 200.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 110.0, "battery_backup_test.after.battery": 80.0, "battery_backup_test.battery_backup_time": 110.0, "comments_recommendation": "all equitment in good conditions.", "technician_name": " ", "technician_id": " ", "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000480674.pdf | 4000480674 | {"station": "CIT", "date_time": "2023-07-23T00:00:00", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 30.0, "general_inspection.readings.B_module_temperature.max": 37.9, "general_inspection.readings.C_battery_run_time": 383.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 239.0, "general_inspection.readings.I_rectifier_voltage.b": 240.0, "general_inspection.readings.I_rectifier_voltage.c": 241.0, "general_inspection.readings.J_bypass_voltage.a": 240.0, "general_inspection.readings.J_bypass_voltage.b": 239.0, "general_inspection.readings.J_bypass_voltage.c": 241.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 240.0, "general_inspection.readings.L_output_current.b": 239.0, "general_inspection.readings.L_output_current.c": 239.0, "general_inspection.readings.M_active_power.a": 1.1, "general_inspection.readings.M_active_power.b": 1.9, "general_inspection.readings.M_active_power.c": 3.9, "general_inspection.readings.N_reactive_power.a": 0.2, "general_inspection.readings.N_reactive_power.b": 0.5, "general_inspection.readings.N_reactive_power.c": 0.9, "general_inspection.readings.O_apparent_power.a": 0.1, "general_inspection.readings.O_apparent_power.b": 0.0, "general_inspection.readings.O_apparent_power.c": 0.1, "general_inspection.readings.P_output_power.a": 0.2, "general_inspection.readings.P_output_power.b": 0.5, "general_inspection.readings.P_output_power.c": 0.9, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.7, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.5, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.4, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 380.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 180.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 150.0, "comments_recommendation": "Ok", "technician_name": " SYAHRUL AZWAN", "technician_id": 7110, "supervisor_name": "AZHAR YUNUS", "supervisor_id": 7111}
SC_PM_NA_UPS_NA_7.pdf |  | {"station": "CIT", "date_time": "23/11/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 30.2, "general_inspection.readings.B_module_temperature.max": 34.5, "general_inspection.readings.C_battery_run_time": 377.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 245.0, "general_inspection.readings.I_rectifier_voltage.b": 243.0, "general_inspection.readings.I_rectifier_voltage.c": 246.0, "general_inspection.readings.J_bypass_voltage.a": 245.0, "general_inspection.readings.J_bypass_voltage.b": 243.0, "general_inspection.readings.J_bypass_voltage.c": 247.0, "general_inspection.readings.K_output_voltage.a": null, "general_inspection.readings.K_output_voltage.b": null, "general_inspection.readings.K_output_voltage.c": null, "general_inspection.readings.L_output_current.a": 1.2, "general_inspection.readings.L_output_current.b": 2.0, "general_inspection.readings.L_output_current.c": 3.9, "general_inspection.readings.M_active_power.a": 0.2, "general_inspection.readings.M_active_power.b": 0.5, "general_inspection.readings.M_active_power.c": 0.9, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.4, "general_inspection.readings.O_apparent_power.c": 0.9, "general_inspection.readings.P_output_power.a": 4.0, "general_inspection.readings.P_output_power.b": 7.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "ALL EQUIPMENTS ARE IN GOOD CONDITION", "technician_name": "", "technician_id": 21970, "supervisor_name": "", "supervisor_id": 7223}
SC_PM_QTR_UPS_4000646748.pdf | 4000646748 | {"station": "CIT", "date_time": "23/10/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 34.5, "general_inspection.readings.B_module_temperature.max": 37.5, "general_inspection.readings.C_battery_run_time": 379.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 299.0, "general_inspection.readings.I_rectifier_voltage.b": 248.0, "general_inspection.readings.I_rectifier_voltage.c": 250.0, "general_inspection.readings.J_bypass_voltage.a": 299.0, "general_inspection.readings.J_bypass_voltage.b": 247.0, "general_inspection.readings.J_bypass_voltage.c": 250.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 1.2, "general_inspection.readings.L_output_current.b": 1.9, "general_inspection.readings.L_output_current.c": 3.6, "general_inspection.readings.M_active_power.a": 0.2, "general_inspection.readings.M_active_power.b": 0.5, "general_inspection.readings.M_active_power.c": 0.8, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.2, "general_inspection.readings.O_apparent_power.b": 0.5, "general_inspection.readings.O_apparent_power.c": 0.9, "general_inspection.readings.P_output_power.a": 4.0, "general_inspection.readings.P_output_power.b": 6.0, "general_inspection.readings.P_output_power.c": 13.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "replace for unit new battery-madule in good condition", "technician_name": "", "technician_id": 19925, "supervisor_name": "", "supervisor_id": 7256}
SC_PM_QTR_UPS_4000576119.pdf | 4000576119 | {"station": "CIT", "date_time": "23/10/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 38.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 365.0, "general_inspection.readings.D_output_frequency": 50.03, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 250.0, "general_inspection.readings.I_rectifier_voltage.b": 249.0, "general_inspection.readings.I_rectifier_voltage.c": 250.0, "general_inspection.readings.J_bypass_voltage.a": 250.0, "general_inspection.readings.J_bypass_voltage.b": 249.0, "general_inspection.readings.J_bypass_voltage.c": 251.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 1.3, "general_inspection.readings.L_output_current.b": 2.0, "general_inspection.readings.L_output_current.c": 3.9, "general_inspection.readings.M_active_power.a": 0.2, "general_inspection.readings.M_active_power.b": 0.4, "general_inspection.readings.M_active_power.c": 0.9, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.5, "general_inspection.readings.O_apparent_power.c": 0.9, "general_inspection.readings.P_output_power.a": 4.0, "general_inspection.readings.P_output_power.b": 6.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "Time For both module not same \n Module 1 2h 25m and module 2 6h 5m", "technician_name": "", "technician_id": 7110, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000493761.pdf | 4000493761 | {"station": "CIT", "date_time": "23/10/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 28.5, "general_inspection.readings.B_module_temperature.max": 35.0, "general_inspection.readings.C_battery_run_time": 376.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 248.0, "general_inspection.readings.I_rectifier_voltage.b": 247.0, "general_inspection.readings.I_rectifier_voltage.c": 245.0, "general_inspection.readings.J_bypass_voltage.a": 248.0, "general_inspection.readings.J_bypass_voltage.b": 247.0, "general_inspection.readings.J_bypass_voltage.c": 249.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 1.1, "general_inspection.readings.L_output_current.b": 2.1, "general_inspection.readings.L_output_current.c": 4.1, "general_inspection.readings.M_active_power.a": 0.2, "general_inspection.readings.M_active_power.b": 0.4, "general_inspection.readings.M_active_power.c": 0.9, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 1.0, "general_inspection.readings.N_reactive_power.c": 0.0, "general_inspection.readings.O_apparent_power.a": 0.2, "general_inspection.readings.O_apparent_power.b": 0.4, "general_inspection.readings.O_apparent_power.c": 0.9, "general_inspection.readings.P_output_power.a": 4.0, "general_inspection.readings.P_output_power.b": 6.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.8, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.7, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.8, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 380.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 180.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 180.0, "comments_recommendation": "all equipment in good conditions", "technician_name": "", "technician_id": 11727, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000660367.pdf | 4000660367 | {"station": "CIT", "date_time": "2025-01-23T00:00:00", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 27.7, "general_inspection.readings.B_module_temperature.max": 33.8, "general_inspection.readings.C_battery_run_time": 377.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 246.0, "general_inspection.readings.I_rectifier_voltage.b": 245.0, "general_inspection.readings.I_rectifier_voltage.c": 247.0, "general_inspection.readings.J_bypass_voltage.a": 246.0, "general_inspection.readings.J_bypass_voltage.b": 245.0, "general_inspection.readings.J_bypass_voltage.c": 248.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 1.1, "general_inspection.readings.L_output_current.b": 2.2, "general_inspection.readings.L_output_current.c": 3.6, "general_inspection.readings.M_active_power.a": 0.2, "general_inspection.readings.M_active_power.b": 0.4, "general_inspection.readings.M_active_power.c": 0.8, "general_inspection.readings.N_reactive_power.a": 1.0, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.4, "general_inspection.readings.O_apparent_power.c": 0.8, "general_inspection.readings.P_output_power.a": 4.0, "general_inspection.readings.P_output_power.b": 7.0, "general_inspection.readings.P_output_power.c": 13.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "UPS in a good condition.", "technician_name": "", "technician_id": 22777, "supervisor_name": "", "supervisor_id": 7222}
SC_PM_QTR_UPS_4000555052.pdf | 4000555052 | {"station": "CIT", "date_time": "23/07/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 110.0, "general_inspection.readings.B_module_temperature.min": 37.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 165.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 272.0, "general_inspection.readings.F_battery_voltage_v.negative": 272.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 244.0, "general_inspection.readings.I_rectifier_voltage.b": null, "general_inspection.readings.I_rectifier_voltage.c": null, "general_inspection.readings.J_bypass_voltage.a": 244.0, "general_inspection.readings.J_bypass_voltage.b": 243.0, "general_inspection.readings.J_bypass_voltage.c": 244.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 2.6, "general_inspection.readings.L_output_current.b": 6.2, "general_inspection.readings.L_output_current.c": 6.8, "general_inspection.readings.M_active_power.a": 0.6, "general_inspection.readings.M_active_power.b": 1.3, "general_inspection.readings.M_active_power.c": 1.6, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 1.2, "general_inspection.readings.O_apparent_power.c": 1.7, "general_inspection.readings.P_output_power.a": 9.0, "general_inspection.readings.P_output_power.b": 19.0, "general_inspection.readings.P_output_power.c": 25.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "", "technician_name": "", "technician_id": 7222, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000608023.pdf | 4000608023 | {"station": "CIT", "date_time": "23/04/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 28.2, "general_inspection.readings.B_module_temperature.max": 34.9, "general_inspection.readings.C_battery_run_time": 369.0, "general_inspection.readings.D_output_frequency": 50.4, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 249.0, "general_inspection.readings.I_rectifier_voltage.b": 248.0, "general_inspection.readings.I_rectifier_voltage.c": 250.0, "general_inspection.readings.J_bypass_voltage.a": 249.0, "general_inspection.readings.J_bypass_voltage.b": 248.0, "general_inspection.readings.J_bypass_voltage.c": 250.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 1.3, "general_inspection.readings.L_output_current.b": 1.8, "general_inspection.readings.L_output_current.c": 3.9, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.4, "general_inspection.readings.M_active_power.c": 0.9, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.4, "general_inspection.readings.O_apparent_power.c": 0.9, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 6.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "(D01-D10) 1 battery faulty", "technician_name": "", "technician_id": 21048, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000530672.pdf | 4000530672 | {"station": "CIT", "date_time": "23/04/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 28.5, "general_inspection.readings.B_module_temperature.max": 35.0, "general_inspection.readings.C_battery_run_time": 375.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.8, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 248.0, "general_inspection.readings.I_rectifier_voltage.b": 247.0, "general_inspection.readings.I_rectifier_voltage.c": 245.0, "general_inspection.readings.J_bypass_voltage.a": 248.0, "general_inspection.readings.J_bypass_voltage.b": 247.0, "general_inspection.readings.J_bypass_voltage.c": 249.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 235.0, "general_inspection.readings.L_output_current.a": 1.1, "general_inspection.readings.L_output_current.b": 2.1, "general_inspection.readings.L_output_current.c": 4.1, "general_inspection.readings.M_active_power.a": 0.2, "general_inspection.readings.M_active_power.b": 0.4, "general_inspection.readings.M_active_power.c": 0.9, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 1.0, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.2, "general_inspection.readings.O_apparent_power.b": 0.4, "general_inspection.readings.O_apparent_power.c": 0.9, "general_inspection.readings.P_output_power.a": 4.0, "general_inspection.readings.P_output_power.b": 6.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.5, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.8, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 81.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 180.0, "battery_backup_test.after.battery": 10.0, "battery_backup_test.battery_backup_time": 180.0, "comments_recommendation": "Good Condition", "technician_name": "", "technician_id": 7110, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000467073.pdf | 4000467073 | {"station": "CIT", "date_time": "23/04/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 37.1, "general_inspection.readings.B_module_temperature.max": 44.8, "general_inspection.readings.C_battery_run_time": 307.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 268.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 242.0, "general_inspection.readings.I_rectifier_voltage.b": 242.0, "general_inspection.readings.I_rectifier_voltage.c": 249.0, "general_inspection.readings.J_bypass_voltage.a": 248.0, "general_inspection.readings.J_bypass_voltage.b": 249.0, "general_inspection.readings.J_bypass_voltage.c": 240.0, "general_inspection.readings.K_output_voltage.a": 241.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 1.0, "general_inspection.readings.L_output_current.b": 2.0, "general_inspection.readings.L_output_current.c": 3.0, "general_inspection.readings.M_active_power.a": 0.2, "general_inspection.readings.M_active_power.b": 0.4, "general_inspection.readings.M_active_power.c": 0.7, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.2, "general_inspection.readings.O_apparent_power.b": 0.4, "general_inspection.readings.O_apparent_power.c": 0.7, "general_inspection.readings.P_output_power.a": 3.0, "general_inspection.readings.P_output_power.b": 2.0, "general_inspection.readings.P_output_power.c": 11.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.2, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 160.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 80.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 80.0, "comments_recommendation": "ok", "technician_name": "", "technician_id": 7222, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000597714.pdf | 4000597714 | {"station": "CIT", "date_time": "23/01/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 35.4, "general_inspection.readings.B_module_temperature.max": 42.5, "general_inspection.readings.C_battery_run_time": 169.0, "general_inspection.readings.D_output_frequency": 50.05, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 272.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 246.0, "general_inspection.readings.I_rectifier_voltage.b": 246.0, "general_inspection.readings.I_rectifier_voltage.c": 248.0, "general_inspection.readings.J_bypass_voltage.a": 247.0, "general_inspection.readings.J_bypass_voltage.b": 246.0, "general_inspection.readings.J_bypass_voltage.c": 248.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 2.6, "general_inspection.readings.L_output_current.b": 5.7, "general_inspection.readings.L_output_current.c": 7.3, "general_inspection.readings.M_active_power.a": 0.6, "general_inspection.readings.M_active_power.b": 1.4, "general_inspection.readings.M_active_power.c": 1.6, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 1.3, "general_inspection.readings.O_apparent_power.c": 1.7, "general_inspection.readings.P_output_power.a": 10.0, "general_inspection.readings.P_output_power.b": 18.0, "general_inspection.readings.P_output_power.c": 24.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All EQUIPMENT IN A GOOD CONDITION", "technician_name": "", "technician_id": 7248, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000509117.pdf | 4000509117 | {"station": "CIT", "date_time": "23/01/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 28.5, "general_inspection.readings.B_module_temperature.max": 35.0, "general_inspection.readings.C_battery_run_time": 375.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.8, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 248.0, "general_inspection.readings.I_rectifier_voltage.b": 247.0, "general_inspection.readings.I_rectifier_voltage.c": 245.0, "general_inspection.readings.J_bypass_voltage.a": 248.0, "general_inspection.readings.J_bypass_voltage.b": 247.0, "general_inspection.readings.J_bypass_voltage.c": 244.0, "general_inspection.readings.K_output_voltage.a": null, "general_inspection.readings.K_output_voltage.b": null, "general_inspection.readings.K_output_voltage.c": null, "general_inspection.readings.L_output_current.a": 1.1, "general_inspection.readings.L_output_current.b": 2.1, "general_inspection.readings.L_output_current.c": 4.1, "general_inspection.readings.M_active_power.a": 2.0, "general_inspection.readings.M_active_power.b": 0.4, "general_inspection.readings.M_active_power.c": 0.9, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 10.0, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.2, "general_inspection.readings.O_apparent_power.b": 0.4, "general_inspection.readings.O_apparent_power.c": 0.9, "general_inspection.readings.P_output_power.a": 4.0, "general_inspection.readings.P_output_power.b": 6.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.5, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.8, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 180.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 180.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 180.0, "comments_recommendation": "", "technician_name": "", "technician_id": 7223, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000446359.pdf | 4000446359 | {"station": "CIT", "date_time": "23/01/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 37.1, "general_inspection.readings.B_module_temperature.max": 44.8, "general_inspection.readings.C_battery_run_time": 307.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 268.0, "general_inspection.readings.F_battery_voltage_v.negative": 269.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 240.0, "general_inspection.readings.I_rectifier_voltage.b": 248.0, "general_inspection.readings.I_rectifier_voltage.c": 249.0, "general_inspection.readings.J_bypass_voltage.a": 248.0, "general_inspection.readings.J_bypass_voltage.b": 249.0, "general_inspection.readings.J_bypass_voltage.c": 240.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 1.0, "general_inspection.readings.L_output_current.b": 2.0, "general_inspection.readings.L_output_current.c": 3.0, "general_inspection.readings.M_active_power.a": 0.2, "general_inspection.readings.M_active_power.b": 0.4, "general_inspection.readings.M_active_power.c": 0.7, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.2, "general_inspection.readings.O_apparent_power.b": 0.4, "general_inspection.readings.O_apparent_power.c": 0.7, "general_inspection.readings.P_output_power.a": 3.0, "general_inspection.readings.P_output_power.b": 2.0, "general_inspection.readings.P_output_power.c": 11.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.2, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 120.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 60.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 120.0, "comments_recommendation": "ok", "technician_name": "", "technician_id": 7223, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000509068.pdf | 4000509068 | {"station": "MKU", "date_time": "22/04/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 36.6, "general_inspection.readings.B_module_temperature.max": 42.6, "general_inspection.readings.C_battery_run_time": 306.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 262.0, "general_inspection.readings.F_battery_voltage_v.negative": 262.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 243.0, "general_inspection.readings.I_rectifier_voltage.b": 242.0, "general_inspection.readings.I_rectifier_voltage.c": 244.0, "general_inspection.readings.J_bypass_voltage.a": 243.0, "general_inspection.readings.J_bypass_voltage.b": 242.0, "general_inspection.readings.J_bypass_voltage.c": 244.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.4, "general_inspection.readings.L_output_current.b": 3.3, "general_inspection.readings.L_output_current.c": 3.6, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.7, "general_inspection.readings.M_active_power.c": 0.78, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.8, "general_inspection.readings.O_apparent_power.c": 0.8, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 12.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.4, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 160.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 80.0, "battery_backup_test.after.battery": 150.0, "battery_backup_test.battery_backup_time": 80.0, "comments_recommendation": "ok", "technician_name": "", "technician_id": "7222", "supervisor_name": "", "supervisor_id": "7111"}
SC_PM_NA_UPS_NA_1 (4).pdf |  | {"station": "Mku", "date_time": "22/11/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 37.3, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 238.0, "general_inspection.readings.D_output_frequency": 50.04, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 268.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 238.0, "general_inspection.readings.I_rectifier_voltage.b": 238.0, "general_inspection.readings.I_rectifier_voltage.c": 239.0, "general_inspection.readings.J_bypass_voltage.a": 238.0, "general_inspection.readings.J_bypass_voltage.b": 238.0, "general_inspection.readings.J_bypass_voltage.c": 239.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.6, "general_inspection.readings.L_output_current.b": 5.3, "general_inspection.readings.L_output_current.c": 3.8, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 1.2, "general_inspection.readings.M_active_power.c": 1.0, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.3, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.2, "general_inspection.readings.O_apparent_power.c": 0.9, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 19.0, "general_inspection.readings.P_output_power.c": 15.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "ALL EQUIPMENT IN GOOD CONDITION", "technician_name": "", "technician_id": 7248, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_NA_UPS_NA_2 (3).pdf |  | {"station": "MKU", "date_time": "22/10/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": null, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 32.5, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 259.0, "general_inspection.readings.D_output_frequency": 50.05, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 268.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 237.0, "general_inspection.readings.I_rectifier_voltage.b": 236.0, "general_inspection.readings.I_rectifier_voltage.c": 238.0, "general_inspection.readings.J_bypass_voltage.a": 237.0, "general_inspection.readings.J_bypass_voltage.b": 237.0, "general_inspection.readings.J_bypass_voltage.c": 239.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 1.6, "general_inspection.readings.L_output_current.b": 4.4, "general_inspection.readings.L_output_current.c": 3.7, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 1.1, "general_inspection.readings.M_active_power.c": 0.8, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.4, "general_inspection.readings.O_apparent_power.b": 1.0, "general_inspection.readings.O_apparent_power.c": 1.8, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 16.0, "general_inspection.readings.P_output_power.c": 12.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All battery in good condition and perform very well.", "technician_name": "", "technician_id": 11727, "supervisor_name": "", "supervisor_id": 7256}
SC_PM_NA_UPS_NA_3.pdf |  | {"station": "Mku", "date_time": "22/10/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 260.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 268.0, "general_inspection.readings.F_battery_voltage_v.negative": 269.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 239.0, "general_inspection.readings.I_rectifier_voltage.b": 240.0, "general_inspection.readings.I_rectifier_voltage.c": 241.0, "general_inspection.readings.J_bypass_voltage.a": 240.0, "general_inspection.readings.J_bypass_voltage.b": 231.0, "general_inspection.readings.J_bypass_voltage.c": 241.0, "general_inspection.readings.K_output_voltage.a": 234.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 241.0, "general_inspection.readings.L_output_current.a": 1.6, "general_inspection.readings.L_output_current.b": 4.7, "general_inspection.readings.L_output_current.c": 3.7, "general_inspection.readings.M_active_power.a": 0.4, "general_inspection.readings.M_active_power.b": 1.0, "general_inspection.readings.M_active_power.c": 0.8, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.1, "general_inspection.readings.O_apparent_power.c": 0.8, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 15.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "-all equipment in good condition\n-all cable tigth and secure", "technician_name": "", "technician_id": 7119, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000509070.pdf | 4000509070 | {"station": "MKU", "date_time": "22/10/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 31.3, "general_inspection.readings.B_module_temperature.max": 38.2, "general_inspection.readings.C_battery_run_time": 241.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 268.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 234.0, "general_inspection.readings.I_rectifier_voltage.b": 233.0, "general_inspection.readings.I_rectifier_voltage.c": 235.0, "general_inspection.readings.J_bypass_voltage.a": 234.0, "general_inspection.readings.J_bypass_voltage.b": 233.0, "general_inspection.readings.J_bypass_voltage.c": 235.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.6, "general_inspection.readings.L_output_current.b": 4.7, "general_inspection.readings.L_output_current.c": 3.7, "general_inspection.readings.M_active_power.a": 0.4, "general_inspection.readings.M_active_power.b": 1.0, "general_inspection.readings.M_active_power.c": 0.8, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.1, "general_inspection.readings.O_apparent_power.c": 0.8, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 15.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.5, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.6, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 240.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 100.0, "battery_backup_test.after.battery": 80.0, "battery_backup_test.battery_backup_time": 100.0, "comments_recommendation": "Good Condition", "technician_name": "", "technician_id": 7223, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_NA_UPS_NA (6).pdf |  | {"station": "MKU", "date_time": "22/07/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 29.0, "general_inspection.readings.B_module_temperature.max": 33.5, "general_inspection.readings.C_battery_run_time": 265.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 26.9, "general_inspection.readings.F_battery_voltage_v.negative": 26.9, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 237.0, "general_inspection.readings.I_rectifier_voltage.b": 236.0, "general_inspection.readings.I_rectifier_voltage.c": 240.0, "general_inspection.readings.J_bypass_voltage.a": 237.0, "general_inspection.readings.J_bypass_voltage.b": 236.0, "general_inspection.readings.J_bypass_voltage.c": 240.0, "general_inspection.readings.K_output_voltage.a": null, "general_inspection.readings.K_output_voltage.b": null, "general_inspection.readings.K_output_voltage.c": null, "general_inspection.readings.L_output_current.a": 1.45, "general_inspection.readings.L_output_current.b": 4.5, "general_inspection.readings.L_output_current.c": 3.5, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 1.0, "general_inspection.readings.M_active_power.c": 0.8, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.0, "general_inspection.readings.O_apparent_power.c": 0.8, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 17.0, "general_inspection.readings.P_output_power.c": 13.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All batteries in good condition.", "technician_name": "", "technician_id": 22153, "supervisor_name": "", "supervisor_id": 7223}
SC_PM_NA_UPS_NA_2 (1).pdf |  | {"station": "MKU", "date_time": "22/07/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 31.3, "general_inspection.readings.B_module_temperature.max": 38.2, "general_inspection.readings.C_battery_run_time": 260.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 218.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 234.0, "general_inspection.readings.I_rectifier_voltage.b": 233.0, "general_inspection.readings.I_rectifier_voltage.c": 235.0, "general_inspection.readings.J_bypass_voltage.a": 234.0, "general_inspection.readings.J_bypass_voltage.b": 233.0, "general_inspection.readings.J_bypass_voltage.c": 235.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.6, "general_inspection.readings.L_output_current.b": 4.7, "general_inspection.readings.L_output_current.c": 3.7, "general_inspection.readings.M_active_power.a": 0.4, "general_inspection.readings.M_active_power.b": 1.0, "general_inspection.readings.M_active_power.c": 0.8, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.1, "general_inspection.readings.O_apparent_power.c": 0.8, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 15.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "", "technician_name": "", "technician_id": 7222, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000509069.pdf | 4000509069 | {"station": "MKU", "date_time": "22/07/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 31.2, "general_inspection.readings.B_module_temperature.max": 37.9, "general_inspection.readings.C_battery_run_time": 247.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 265.0, "general_inspection.readings.F_battery_voltage_v.negative": 269.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 237.0, "general_inspection.readings.I_rectifier_voltage.b": 237.0, "general_inspection.readings.I_rectifier_voltage.c": 239.0, "general_inspection.readings.J_bypass_voltage.a": 237.0, "general_inspection.readings.J_bypass_voltage.b": 236.0, "general_inspection.readings.J_bypass_voltage.c": 234.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 1.6, "general_inspection.readings.L_output_current.b": 4.5, "general_inspection.readings.L_output_current.c": 3.7, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 1.0, "general_inspection.readings.M_active_power.c": 0.9, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.1, "general_inspection.readings.O_apparent_power.c": 0.8, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 16.0, "general_inspection.readings.P_output_power.c": 12.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.6, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 240.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 100.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 200.0, "comments_recommendation": "all equitment in good conditions", "technician_name": "", "technician_id": 11727, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_NA_UPS_NA_1 (5).pdf |  | {"station": "MKU", "date_time": "22/04/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": null, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 22.5, "general_inspection.readings.B_module_temperature.max": 23.8, "general_inspection.readings.C_battery_run_time": 238.0, "general_inspection.readings.D_output_frequency": 50.03, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 268.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 240.0, "general_inspection.readings.I_rectifier_voltage.b": 236.0, "general_inspection.readings.I_rectifier_voltage.c": 242.0, "general_inspection.readings.J_bypass_voltage.a": 240.0, "general_inspection.readings.J_bypass_voltage.b": 238.0, "general_inspection.readings.J_bypass_voltage.c": 242.0, "general_inspection.readings.K_output_voltage.a": null, "general_inspection.readings.K_output_voltage.b": null, "general_inspection.readings.K_output_voltage.c": null, "general_inspection.readings.L_output_current.a": 1.6, "general_inspection.readings.L_output_current.b": 5.1, "general_inspection.readings.L_output_current.c": 4.3, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 1.0, "general_inspection.readings.M_active_power.c": 0.8, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.4, "general_inspection.readings.N_reactive_power.c": 0.4, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.2, "general_inspection.readings.O_apparent_power.c": 1.0, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 18.0, "general_inspection.readings.P_output_power.c": 15.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All batteries and module in good condition.", "technician_name": "", "technician_id": 19921, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_NA_UPS_NA (2).pdf |  | {"station": "MKU", "date_time": "22/04/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 31.3, "general_inspection.readings.B_module_temperature.max": 38.2, "general_inspection.readings.C_battery_run_time": 240.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 268.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 234.0, "general_inspection.readings.I_rectifier_voltage.b": 233.0, "general_inspection.readings.I_rectifier_voltage.c": 235.0, "general_inspection.readings.J_bypass_voltage.a": 234.0, "general_inspection.readings.J_bypass_voltage.b": 233.0, "general_inspection.readings.J_bypass_voltage.c": 235.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.6, "general_inspection.readings.L_output_current.b": 4.7, "general_inspection.readings.L_output_current.c": 3.1, "general_inspection.readings.M_active_power.a": 0.4, "general_inspection.readings.M_active_power.b": 1.0, "general_inspection.readings.M_active_power.c": 0.3, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.8, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.1, "general_inspection.readings.O_apparent_power.c": 0.8, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 15.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.5, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.5, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 200.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 100.0, "battery_backup_test.after.battery": 150.0, "battery_backup_test.battery_backup_time": 100.0, "comments_recommendation": "", "technician_name": "", "technician_id": 7110, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000669552.pdf | 4000669552 | {"station": "MKU", "date_time": "22/01/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": null, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 28.6, "general_inspection.readings.B_module_temperature.max": 35.1, "general_inspection.readings.C_battery_run_time": 246.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 269.0, "general_inspection.readings.F_battery_voltage_v.negative": 269.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 235.0, "general_inspection.readings.I_rectifier_voltage.b": 234.0, "general_inspection.readings.I_rectifier_voltage.c": 236.0, "general_inspection.readings.J_bypass_voltage.a": 235.0, "general_inspection.readings.J_bypass_voltage.b": 234.0, "general_inspection.readings.J_bypass_voltage.c": 236.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 1.6, "general_inspection.readings.L_output_current.b": 4.4, "general_inspection.readings.L_output_current.c": 3.6, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 1.0, "general_inspection.readings.M_active_power.c": 0.8, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.9, "general_inspection.readings.O_apparent_power.b": 1.0, "general_inspection.readings.O_apparent_power.c": 0.9, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 15.0, "general_inspection.readings.P_output_power.c": 13.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "UPS in a good condition.", "technician_name": "", "technician_id": "22776", "supervisor_name": "", "supervisor_id": 7222}
SC_PM_QTR_UPS_4000509072.pdf | 4000509072 | {"station": "Mku", "date_time": "22/01/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 31.3, "general_inspection.readings.B_module_temperature.max": 34.2, "general_inspection.readings.C_battery_run_time": 240.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 269.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 234.0, "general_inspection.readings.I_rectifier_voltage.b": 233.0, "general_inspection.readings.I_rectifier_voltage.c": 235.0, "general_inspection.readings.J_bypass_voltage.a": 234.0, "general_inspection.readings.J_bypass_voltage.b": 233.0, "general_inspection.readings.J_bypass_voltage.c": 235.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.6, "general_inspection.readings.L_output_current.b": 4.7, "general_inspection.readings.L_output_current.c": 3.7, "general_inspection.readings.M_active_power.a": 0.4, "general_inspection.readings.M_active_power.b": 1.1, "general_inspection.readings.M_active_power.c": 0.8, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.1, "general_inspection.readings.O_apparent_power.c": 0.8, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 15.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.5, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.5, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 200.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 100.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 100.0, "comments_recommendation": "", "technician_name": "", "technician_id": "7222", "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000509067.pdf | 4000509067 | {"station": "MKU", "date_time": "22/01/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 36.6, "general_inspection.readings.B_module_temperature.max": 42.6, "general_inspection.readings.C_battery_run_time": 310.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 262.0, "general_inspection.readings.F_battery_voltage_v.negative": 262.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 243.0, "general_inspection.readings.I_rectifier_voltage.b": 242.0, "general_inspection.readings.I_rectifier_voltage.c": 244.0, "general_inspection.readings.J_bypass_voltage.a": 243.0, "general_inspection.readings.J_bypass_voltage.b": 242.0, "general_inspection.readings.J_bypass_voltage.c": 244.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.4, "general_inspection.readings.L_output_current.b": 3.3, "general_inspection.readings.L_output_current.c": 3.6, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.7, "general_inspection.readings.M_active_power.c": 0.8, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.8, "general_inspection.readings.O_apparent_power.c": 0.0, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 12.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.4, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 160.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 80.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 80.0, "comments_recommendation": "OK", "technician_name": "", "technician_id": 7223, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000576104.pdf | 4000576104 | {"station": "BAS", "date_time": "21/10/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 250.0, "general_inspection.readings.D_output_frequency": 50.03, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 247.0, "general_inspection.readings.I_rectifier_voltage.b": 248.0, "general_inspection.readings.I_rectifier_voltage.c": 250.0, "general_inspection.readings.J_bypass_voltage.a": 247.0, "general_inspection.readings.J_bypass_voltage.b": 248.0, "general_inspection.readings.J_bypass_voltage.c": 250.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.4, "general_inspection.readings.L_output_current.b": 3.6, "general_inspection.readings.L_output_current.c": 5.5, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.8, "general_inspection.readings.M_active_power.c": 1.3, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.7, "general_inspection.readings.O_apparent_power.c": 1.3, "general_inspection.readings.P_output_power.a": 3.0, "general_inspection.readings.P_output_power.b": 12.0, "general_inspection.readings.P_output_power.c": 20.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": null, "servicing_and_cleaning.switch_on_maintenance_bypass.status": null, "servicing_and_cleaning.confirm_display_panel.status": null, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": "", "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": null, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": null, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": null, "servicing_and_cleaning.normalized_all_battery_breakers.status": null, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": null, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": null, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": null, "servicing_and_cleaning.check_everything__normal.status": null, "battery_backup_test.check_battery_level.status": null, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": null, "battery_backup_test.turn_off_main_switch_breaker.status": null, "battery_backup_test.confirm_alarm_sounding.status": null, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": null, "battery_backup_test.switch_on_back_main_switch_breaker.status": null, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All equipment in good condition", "technician_name": "", "technician_id": 20160, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000493753.pdf | 4000493753 | {"station": "BAS", "date_time": "21/10/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 31.5, "general_inspection.readings.B_module_temperature.max": 38.4, "general_inspection.readings.C_battery_run_time": 207.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 249.0, "general_inspection.readings.I_rectifier_voltage.b": 249.0, "general_inspection.readings.I_rectifier_voltage.c": 249.0, "general_inspection.readings.J_bypass_voltage.a": 249.0, "general_inspection.readings.J_bypass_voltage.b": 249.0, "general_inspection.readings.J_bypass_voltage.c": 251.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.5, "general_inspection.readings.L_output_current.b": 3.8, "general_inspection.readings.L_output_current.c": 6.0, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.8, "general_inspection.readings.M_active_power.c": 1.4, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.3, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.8, "general_inspection.readings.O_apparent_power.c": 1.4, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 12.0, "general_inspection.readings.P_output_power.c": 22.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.6, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 190.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 100.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 100.0, "comments_recommendation": "Good Condition.", "technician_name": "ROHIZAN", "technician_id": 7223, "supervisor_name": "AZHAR YUNUS", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000597702.pdf | 4000597702 | {"station": "BAS", "date_time": "21/01/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": null, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 31.8, "general_inspection.readings.B_module_temperature.max": 38.3, "general_inspection.readings.C_battery_run_time": 219.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 249.0, "general_inspection.readings.I_rectifier_voltage.b": 248.0, "general_inspection.readings.I_rectifier_voltage.c": 252.0, "general_inspection.readings.J_bypass_voltage.a": 249.0, "general_inspection.readings.J_bypass_voltage.b": 248.0, "general_inspection.readings.J_bypass_voltage.c": 252.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 241.0, "general_inspection.readings.L_output_current.a": 1.5, "general_inspection.readings.L_output_current.b": 4.1, "general_inspection.readings.L_output_current.c": 6.0, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.9, "general_inspection.readings.M_active_power.c": 1.4, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.9, "general_inspection.readings.O_apparent_power.c": 1.5, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 14.0, "general_inspection.readings.P_output_power.c": 23.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "* Battery bank 1 and 2 (A01-040) need to be replaced.\n* Battery is damaged.\n* Battery can only cover 93%\n* Module P02 need to calibrate.", "technician_name": "", "technician_id": "20079", "supervisor_name": "", "supervisor_id": ""}
SC_PM_NA_UPS_NA_1 (6).pdf |  | {"station": "BAS", "date_time": "21/07/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 28.3, "general_inspection.readings.B_module_temperature.max": 32.9, "general_inspection.readings.C_battery_run_time": 268.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 248.0, "general_inspection.readings.I_rectifier_voltage.b": 247.0, "general_inspection.readings.I_rectifier_voltage.c": 252.0, "general_inspection.readings.J_bypass_voltage.a": 248.0, "general_inspection.readings.J_bypass_voltage.b": 247.0, "general_inspection.readings.J_bypass_voltage.c": 252.0, "general_inspection.readings.K_output_voltage.a": null, "general_inspection.readings.K_output_voltage.b": null, "general_inspection.readings.K_output_voltage.c": null, "general_inspection.readings.L_output_current.a": 1.3, "general_inspection.readings.L_output_current.b": 2.9, "general_inspection.readings.L_output_current.c": 5.1, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.6, "general_inspection.readings.M_active_power.c": 1.1, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.7, "general_inspection.readings.O_apparent_power.c": 1.1, "general_inspection.readings.P_output_power.a": 4.0, "general_inspection.readings.P_output_power.b": 11.0, "general_inspection.readings.P_output_power.c": 17.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All equipment are in good condition.", "technician_name": "", "technician_id": 20005, "supervisor_name": "", "supervisor_id": 7223}
SC_PM_QTR_UPS_4000480661.pdf | 4000480661 | {"station": "BAS", "date_time": "21/07/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 31.3, "general_inspection.readings.B_module_temperature.max": 38.3, "general_inspection.readings.C_battery_run_time": 228.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 206.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 249.0, "general_inspection.readings.I_rectifier_voltage.b": 249.0, "general_inspection.readings.I_rectifier_voltage.c": 249.0, "general_inspection.readings.J_bypass_voltage.a": 249.0, "general_inspection.readings.J_bypass_voltage.b": 249.0, "general_inspection.readings.J_bypass_voltage.c": 252.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.5, "general_inspection.readings.L_output_current.b": 3.8, "general_inspection.readings.L_output_current.c": 6.0, "general_inspection.readings.M_active_power.a": 3.0, "general_inspection.readings.M_active_power.b": 9.0, "general_inspection.readings.M_active_power.c": 1.4, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.3, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.8, "general_inspection.readings.O_apparent_power.c": 1.4, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 13.0, "general_inspection.readings.P_output_power.c": 22.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.0, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 190.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 100.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 100.0, "comments_recommendation": "all equipment in good conditions", "technician_name": "", "technician_id": 11727, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000530660.pdf | 4000530660 | {"station": "BAS", "date_time": "2023-04-21T00:00:00", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 31.5, "general_inspection.readings.B_module_temperature.max": 38.4, "general_inspection.readings.C_battery_run_time": 225.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 249.0, "general_inspection.readings.I_rectifier_voltage.b": 249.0, "general_inspection.readings.I_rectifier_voltage.c": 249.0, "general_inspection.readings.J_bypass_voltage.a": 249.0, "general_inspection.readings.J_bypass_voltage.b": 249.0, "general_inspection.readings.J_bypass_voltage.c": 250.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.5, "general_inspection.readings.L_output_current.b": 3.8, "general_inspection.readings.L_output_current.c": 6.0, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.0, "general_inspection.readings.M_active_power.c": 1.4, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.3, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.0, "general_inspection.readings.O_apparent_power.c": 1.4, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 12.0, "general_inspection.readings.P_output_power.c": 22.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.4, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 200.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 100.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 100.0, "comments_recommendation": "", "technician_name": "", "technician_id": 7110, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000608011.pdf | 4000608011 | {"station": "BAS", "date_time": "21/04/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": null, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 33.1, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 238.0, "general_inspection.readings.D_output_frequency": 50.03, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 249.0, "general_inspection.readings.I_rectifier_voltage.b": 248.0, "general_inspection.readings.I_rectifier_voltage.c": 251.0, "general_inspection.readings.J_bypass_voltage.a": 248.0, "general_inspection.readings.J_bypass_voltage.b": 249.0, "general_inspection.readings.J_bypass_voltage.c": 252.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.5, "general_inspection.readings.L_output_current.b": 3.4, "general_inspection.readings.L_output_current.c": 5.6, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.8, "general_inspection.readings.M_active_power.c": 1.3, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.8, "general_inspection.readings.O_apparent_power.c": 1.4, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 12.0, "general_inspection.readings.P_output_power.c": 20.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All module and batteries in good condition.\nOnly using bank 3, bank 1 and 2 temporary\ndoesn't have batteries due expired batteries.", "technician_name": "", "technician_id": 19921, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000467064.pdf | 4000467064 | {"station": "BAS", "date_time": "21/04/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 29.3, "general_inspection.readings.B_module_temperature.max": 36.6, "general_inspection.readings.C_battery_run_time": 272.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 1.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 248.0, "general_inspection.readings.I_rectifier_voltage.b": 248.0, "general_inspection.readings.I_rectifier_voltage.c": 250.0, "general_inspection.readings.J_bypass_voltage.a": 248.0, "general_inspection.readings.J_bypass_voltage.b": 248.0, "general_inspection.readings.J_bypass_voltage.c": 254.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.5, "general_inspection.readings.L_output_current.b": 3.5, "general_inspection.readings.L_output_current.c": 4.5, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.7, "general_inspection.readings.M_active_power.c": 1.0, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.0, "general_inspection.readings.O_apparent_power.c": 1.0, "general_inspection.readings.P_output_power.a": 8.0, "general_inspection.readings.P_output_power.b": 11.0, "general_inspection.readings.P_output_power.c": 16.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 120.0, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.9, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.2, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 180.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 80.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 80.0, "comments_recommendation": "ok", "technician_name": "", "technician_id": 7110, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000660989.pdf | 4000660989 | {"station": "BAS", "date_time": "21/01/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 33.1, "general_inspection.readings.B_module_temperature.max": 39.8, "general_inspection.readings.C_battery_run_time": 243.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 246.0, "general_inspection.readings.I_rectifier_voltage.b": 247.0, "general_inspection.readings.I_rectifier_voltage.c": 249.0, "general_inspection.readings.J_bypass_voltage.a": 246.0, "general_inspection.readings.J_bypass_voltage.b": 246.0, "general_inspection.readings.J_bypass_voltage.c": 249.0, "general_inspection.readings.K_output_voltage.a": 241.0, "general_inspection.readings.K_output_voltage.b": 230.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.4, "general_inspection.readings.L_output_current.b": 3.1, "general_inspection.readings.L_output_current.c": 5.6, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.7, "general_inspection.readings.M_active_power.c": 0.2, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.8, "general_inspection.readings.O_apparent_power.c": 1.3, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 12.0, "general_inspection.readings.P_output_power.c": 19.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "# UPS in a good condition", "technician_name": "", "technician_id": 2276, "supervisor_name": "", "supervisor_id": 7222}
SC_PM_QTR_UPS_4000509125.pdf | 4000509125 | {"station": "BAS", "date_time": "21/01/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 31.5, "general_inspection.readings.B_module_temperature.max": 38.4, "general_inspection.readings.C_battery_run_time": 225.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 249.0, "general_inspection.readings.I_rectifier_voltage.b": 249.0, "general_inspection.readings.I_rectifier_voltage.c": 249.0, "general_inspection.readings.J_bypass_voltage.a": 249.0, "general_inspection.readings.J_bypass_voltage.b": 249.0, "general_inspection.readings.J_bypass_voltage.c": 250.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.5, "general_inspection.readings.L_output_current.b": 3.8, "general_inspection.readings.L_output_current.c": 6.0, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.8, "general_inspection.readings.M_active_power.c": 1.4, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.3, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.8, "general_inspection.readings.O_apparent_power.c": 1.4, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 12.0, "general_inspection.readings.P_output_power.c": 22.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.4, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 200.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 100.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 100.0, "comments_recommendation": "", "technician_name": "", "technician_id": 7222, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000446126.pdf | 4000446126 | {"station": "BAS", "date_time": "21/01/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 29.6, "general_inspection.readings.B_module_temperature.max": 36.6, "general_inspection.readings.C_battery_run_time": 272.0, "general_inspection.readings.D_output_frequency": 80.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 269.0, "general_inspection.readings.F_battery_voltage_v.negative": 269.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 248.0, "general_inspection.readings.I_rectifier_voltage.b": 248.0, "general_inspection.readings.I_rectifier_voltage.c": 250.0, "general_inspection.readings.J_bypass_voltage.a": 248.0, "general_inspection.readings.J_bypass_voltage.b": 248.0, "general_inspection.readings.J_bypass_voltage.c": 250.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.5, "general_inspection.readings.L_output_current.b": 3.5, "general_inspection.readings.L_output_current.c": 4.5, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.7, "general_inspection.readings.M_active_power.c": 1.0, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.6, "general_inspection.readings.O_apparent_power.c": 1.0, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 11.0, "general_inspection.readings.P_output_power.c": 16.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.8, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.9, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.2, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 180.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 80.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 60.0, "comments_recommendation": "♡", "technician_name": "", "technician_id": 7223, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000647410.pdf | 4000647410 | {"station": "RAN", "date_time": "20/10/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 34.1, "general_inspection.readings.B_module_temperature.max": 40.3, "general_inspection.readings.C_battery_run_time": 234.0, "general_inspection.readings.D_output_frequency": 50.03, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 245.0, "general_inspection.readings.I_rectifier_voltage.b": 244.0, "general_inspection.readings.I_rectifier_voltage.c": 245.0, "general_inspection.readings.J_bypass_voltage.a": 244.0, "general_inspection.readings.J_bypass_voltage.b": 243.0, "general_inspection.readings.J_bypass_voltage.c": 246.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 2.2, "general_inspection.readings.L_output_current.b": 4.0, "general_inspection.readings.L_output_current.c": 5.2, "general_inspection.readings.M_active_power.a": 0.5, "general_inspection.readings.M_active_power.b": 0.9, "general_inspection.readings.M_active_power.c": 1.2, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.5, "general_inspection.readings.O_apparent_power.b": 0.8, "general_inspection.readings.O_apparent_power.c": 1.2, "general_inspection.readings.P_output_power.a": 8.0, "general_inspection.readings.P_output_power.b": 13.0, "general_inspection.readings.P_output_power.c": 19.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "Breaker 2 and 3 not function, waiting for new battery", "technician_name": "", "technician_id": "11727", "supervisor_name": "", "supervisor_id": "7256"}
SC_PM_QTR_UPS_4000576174.pdf | 4000576174 | {"station": "RAN", "date_time": "20/10/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": null, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 236.0, "general_inspection.readings.D_output_frequency": 50.02, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 242.0, "general_inspection.readings.I_rectifier_voltage.b": 241.0, "general_inspection.readings.I_rectifier_voltage.c": 244.0, "general_inspection.readings.J_bypass_voltage.a": 243.0, "general_inspection.readings.J_bypass_voltage.b": 241.0, "general_inspection.readings.J_bypass_voltage.c": 244.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.9, "general_inspection.readings.L_output_current.b": 3.7, "general_inspection.readings.L_output_current.c": 4.9, "general_inspection.readings.M_active_power.a": 0.4, "general_inspection.readings.M_active_power.b": 0.8, "general_inspection.readings.M_active_power.c": 1.2, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.4, "general_inspection.readings.O_apparent_power.b": 0.8, "general_inspection.readings.O_apparent_power.c": 1.1, "general_inspection.readings.P_output_power.a": 6.0, "general_inspection.readings.P_output_power.b": 13.0, "general_inspection.readings.P_output_power.c": 18.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": null, "servicing_and_cleaning.switch_off_both_of_module.status": null, "servicing_and_cleaning.open_screw_and_pull_both_module.status": null, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": "", "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": null, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": null, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": null, "servicing_and_cleaning.normalized_all_battery_breakers.status": null, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": null, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": null, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": null, "servicing_and_cleaning.check_everything__normal.status": null, "battery_backup_test.check_battery_level.status": null, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": null, "battery_backup_test.turn_off_main_switch_breaker.status": null, "battery_backup_test.confirm_alarm_sounding.status": null, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": null, "battery_backup_test.switch_on_back_main_switch_breaker.status": null, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All equipment in good condition", "technician_name": "", "technician_id": 20160, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000493784.pdf | 4000493784 | {"station": "RAN", "date_time": "20/10/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 32.7, "general_inspection.readings.B_module_temperature.max": 39.0, "general_inspection.readings.C_battery_run_time": 228.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 242.0, "general_inspection.readings.I_rectifier_voltage.b": 241.0, "general_inspection.readings.I_rectifier_voltage.c": 242.0, "general_inspection.readings.J_bypass_voltage.a": 241.0, "general_inspection.readings.J_bypass_voltage.b": 240.0, "general_inspection.readings.J_bypass_voltage.c": 241.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 2.1, "general_inspection.readings.L_output_current.b": 3.8, "general_inspection.readings.L_output_current.c": 5.3, "general_inspection.readings.M_active_power.a": 0.5, "general_inspection.readings.M_active_power.b": 0.8, "general_inspection.readings.M_active_power.c": 1.2, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.5, "general_inspection.readings.O_apparent_power.b": 0.8, "general_inspection.readings.O_apparent_power.c": 1.2, "general_inspection.readings.P_output_power.a": 7.0, "general_inspection.readings.P_output_power.b": 12.0, "general_inspection.readings.P_output_power.c": 19.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.3, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.6, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 180.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 90.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 90.0, "comments_recommendation": "Good Condition.", "technician_name": "", "technician_id": 7223, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000480709.pdf | 4000480709 | {"station": "RAN", "date_time": "2022-07-20T00:00:00", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 34.5, "general_inspection.readings.B_module_temperature.max": 40.6, "general_inspection.readings.C_battery_run_time": 217.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 242.0, "general_inspection.readings.I_rectifier_voltage.b": 241.0, "general_inspection.readings.I_rectifier_voltage.c": 244.0, "general_inspection.readings.J_bypass_voltage.a": 241.0, "general_inspection.readings.J_bypass_voltage.b": 240.0, "general_inspection.readings.J_bypass_voltage.c": 243.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 131.0, "general_inspection.readings.K_output_voltage.c": 7.0, "general_inspection.readings.L_output_current.a": 2.2, "general_inspection.readings.L_output_current.b": 3.4, "general_inspection.readings.L_output_current.c": 5.5, "general_inspection.readings.M_active_power.a": 0.5, "general_inspection.readings.M_active_power.b": 0.8, "general_inspection.readings.M_active_power.c": 1.2, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.5, "general_inspection.readings.O_apparent_power.b": 0.9, "general_inspection.readings.O_apparent_power.c": 1.1, "general_inspection.readings.P_output_power.a": 8.0, "general_inspection.readings.P_output_power.b": 12.0, "general_inspection.readings.P_output_power.c": 18.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.6, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 100.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 90.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 90.0, "comments_recommendation": "all equitment in good conditions", "technician_name": " ABDUL AZIN", "technician_id": 11727, "supervisor_name": "AZHAR YUNUS", "supervisor_id": 7111}
SC_PM_NA_UPS_NA_11.pdf |  | {"station": "RAN", "date_time": "20/07/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 37.7, "general_inspection.readings.B_module_temperature.max": 43.7, "general_inspection.readings.C_battery_run_time": 220.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 243.0, "general_inspection.readings.I_rectifier_voltage.b": 243.0, "general_inspection.readings.I_rectifier_voltage.c": 245.0, "general_inspection.readings.J_bypass_voltage.a": 244.0, "general_inspection.readings.J_bypass_voltage.b": 243.0, "general_inspection.readings.J_bypass_voltage.c": 246.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 2.2, "general_inspection.readings.L_output_current.b": 3.9, "general_inspection.readings.L_output_current.c": 5.5, "general_inspection.readings.M_active_power.a": 0.5, "general_inspection.readings.M_active_power.b": 0.9, "general_inspection.readings.M_active_power.c": 1.2, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.5, "general_inspection.readings.O_apparent_power.b": 0.9, "general_inspection.readings.O_apparent_power.c": 1.3, "general_inspection.readings.P_output_power.a": 7.0, "general_inspection.readings.P_output_power.b": 15.0, "general_inspection.readings.P_output_power.c": 19.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "Battery in good condition and all cable at bank properly connected", "technician_name": "", "technician_id": 20160, "supervisor_name": "", "supervisor_id": 7223}
SC_PM_QTR_UPS_4000555093.pdf | 4000555093 | {"station": "RAN", "date_time": "20/07/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 33.8, "general_inspection.readings.B_module_temperature.max": 39.0, "general_inspection.readings.C_battery_run_time": 229.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 242.0, "general_inspection.readings.I_rectifier_voltage.b": 241.0, "general_inspection.readings.I_rectifier_voltage.c": 242.0, "general_inspection.readings.J_bypass_voltage.a": 241.0, "general_inspection.readings.J_bypass_voltage.b": 240.0, "general_inspection.readings.J_bypass_voltage.c": 242.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 2.1, "general_inspection.readings.L_output_current.b": 3.8, "general_inspection.readings.L_output_current.c": 5.3, "general_inspection.readings.M_active_power.a": 0.5, "general_inspection.readings.M_active_power.b": 0.8, "general_inspection.readings.M_active_power.c": 1.2, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.5, "general_inspection.readings.O_apparent_power.b": 0.8, "general_inspection.readings.O_apparent_power.c": 1.3, "general_inspection.readings.P_output_power.a": 7.0, "general_inspection.readings.P_output_power.b": 12.0, "general_inspection.readings.P_output_power.c": 19.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "", "technician_name": "", "technician_id": 7222, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000608067.pdf | 4000608067 | {"station": "RAN", "date_time": "20/04/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 36.8, "general_inspection.readings.B_module_temperature.max": 41.5, "general_inspection.readings.C_battery_run_time": 230.0, "general_inspection.readings.D_output_frequency": 50.04, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 242.0, "general_inspection.readings.I_rectifier_voltage.b": 242.0, "general_inspection.readings.I_rectifier_voltage.c": 244.0, "general_inspection.readings.J_bypass_voltage.a": 243.0, "general_inspection.readings.J_bypass_voltage.b": 241.0, "general_inspection.readings.J_bypass_voltage.c": 244.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.8, "general_inspection.readings.L_output_current.b": 3.8, "general_inspection.readings.L_output_current.c": 5.3, "general_inspection.readings.M_active_power.a": 0.4, "general_inspection.readings.M_active_power.b": 0.8, "general_inspection.readings.M_active_power.c": 1.3, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.4, "general_inspection.readings.O_apparent_power.b": 0.9, "general_inspection.readings.O_apparent_power.c": 1.2, "general_inspection.readings.P_output_power.a": 6.0, "general_inspection.readings.P_output_power.b": 14.0, "general_inspection.readings.P_output_power.c": 19.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "Module and battenes in good condition.\nBank 2 and 3 don't have batteries Only\nused Bank 1.", "technician_name": "", "technician_id": 19921, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000530706.pdf | 4000530706 | {"station": "RAN", "date_time": "20/04/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 33.4, "general_inspection.readings.B_module_temperature.max": 34.6, "general_inspection.readings.C_battery_run_time": 246.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 268.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 234.0, "general_inspection.readings.I_rectifier_voltage.b": 234.0, "general_inspection.readings.I_rectifier_voltage.c": 240.0, "general_inspection.readings.J_bypass_voltage.a": 236.0, "general_inspection.readings.J_bypass_voltage.b": 238.0, "general_inspection.readings.J_bypass_voltage.c": 236.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.6, "general_inspection.readings.L_output_current.b": 4.5, "general_inspection.readings.L_output_current.c": 3.7, "general_inspection.readings.M_active_power.a": 0.4, "general_inspection.readings.M_active_power.b": 1.0, "general_inspection.readings.M_active_power.c": 0.8, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.1, "general_inspection.readings.O_apparent_power.c": 0.8, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 15.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.2, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.8, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.6, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 200.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 100.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 100.0, "comments_recommendation": "all equipment in good conditions", "technician_name": "", "technician_id": 11727, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000467101.pdf | 4000467101 | {"station": "RAN", "date_time": "20/04/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 49.5, "general_inspection.readings.B_module_temperature.max": 32.5, "general_inspection.readings.C_battery_run_time": 150.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 298.0, "general_inspection.readings.F_battery_voltage_v.negative": 282.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 246.0, "general_inspection.readings.I_rectifier_voltage.b": 247.0, "general_inspection.readings.I_rectifier_voltage.c": 249.0, "general_inspection.readings.J_bypass_voltage.a": 282.0, "general_inspection.readings.J_bypass_voltage.b": 281.0, "general_inspection.readings.J_bypass_voltage.c": 283.0, "general_inspection.readings.K_output_voltage.a": 244.0, "general_inspection.readings.K_output_voltage.b": 242.0, "general_inspection.readings.K_output_voltage.c": 241.0, "general_inspection.readings.L_output_current.a": 0.1, "general_inspection.readings.L_output_current.b": 0.1, "general_inspection.readings.L_output_current.c": 0.2, "general_inspection.readings.M_active_power.a": 1.0, "general_inspection.readings.M_active_power.b": 1.1, "general_inspection.readings.M_active_power.c": 1.2, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.5, "general_inspection.readings.O_apparent_power.a": 0.4, "general_inspection.readings.O_apparent_power.b": 0.7, "general_inspection.readings.O_apparent_power.c": 0.6, "general_inspection.readings.P_output_power.a": 8.0, "general_inspection.readings.P_output_power.b": 16.0, "general_inspection.readings.P_output_power.c": 23.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.8, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 15.2, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.6, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 120.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 80.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 80.0, "comments_recommendation": "ok", "technician_name": "", "technician_id": 7110, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000668095.pdf | 4000668095 | {"station": "RAN", "date_time": "20/01/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 36.8, "general_inspection.readings.B_module_temperature.max": 43.0, "general_inspection.readings.C_battery_run_time": 237.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 241.0, "general_inspection.readings.I_rectifier_voltage.b": 240.0, "general_inspection.readings.I_rectifier_voltage.c": 243.0, "general_inspection.readings.J_bypass_voltage.a": 241.0, "general_inspection.readings.J_bypass_voltage.b": 240.0, "general_inspection.readings.J_bypass_voltage.c": 243.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 2.0, "general_inspection.readings.L_output_current.b": 4.1, "general_inspection.readings.L_output_current.c": 4.9, "general_inspection.readings.M_active_power.a": 0.5, "general_inspection.readings.M_active_power.b": 0.9, "general_inspection.readings.M_active_power.c": 1.2, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.3, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.5, "general_inspection.readings.O_apparent_power.b": 1.0, "general_inspection.readings.O_apparent_power.c": 1.2, "general_inspection.readings.P_output_power.a": 7.0, "general_inspection.readings.P_output_power.b": 13.0, "general_inspection.readings.P_output_power.c": 17.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "Only one bank (Bank A and Bank B)\nOther that, all equipment in a good conditions.", "technician_name": "", "technician_id": 22777, "supervisor_name": "", "supervisor_id": 7222}
SC_PM_QTR_UPS_4000597864.pdf | 4000597864 | {"station": "RAN", "date_time": "20/01/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 31.1, "general_inspection.readings.B_module_temperature.max": 37.1, "general_inspection.readings.C_battery_run_time": 230.0, "general_inspection.readings.D_output_frequency": 50.08, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 243.0, "general_inspection.readings.I_rectifier_voltage.b": 242.0, "general_inspection.readings.I_rectifier_voltage.c": 245.0, "general_inspection.readings.J_bypass_voltage.a": 242.0, "general_inspection.readings.J_bypass_voltage.b": 242.0, "general_inspection.readings.J_bypass_voltage.c": 245.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 2.0, "general_inspection.readings.L_output_current.b": 3.7, "general_inspection.readings.L_output_current.c": 5.3, "general_inspection.readings.M_active_power.a": 0.4, "general_inspection.readings.M_active_power.b": 0.9, "general_inspection.readings.M_active_power.c": 1.2, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.5, "general_inspection.readings.O_apparent_power.b": 1.0, "general_inspection.readings.O_apparent_power.c": 1.2, "general_inspection.readings.P_output_power.a": 7.0, "general_inspection.readings.P_output_power.b": 13.0, "general_inspection.readings.P_output_power.c": 18.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "- Battery Bank 3 (EO1 - F40) need to be replaced\n- Battery 3 value is below 12V (EO1 - F40)", "technician_name": "", "technician_id": 20079, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000509057.pdf | 4000509057 | {"station": "RAN", "date_time": "20/01/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 32.7, "general_inspection.readings.B_module_temperature.max": 39.0, "general_inspection.readings.C_battery_run_time": 208.8, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.1, "general_inspection.readings.I_rectifier_voltage.a": 242.0, "general_inspection.readings.I_rectifier_voltage.b": 241.0, "general_inspection.readings.I_rectifier_voltage.c": 242.0, "general_inspection.readings.J_bypass_voltage.a": 241.0, "general_inspection.readings.J_bypass_voltage.b": 240.0, "general_inspection.readings.J_bypass_voltage.c": 242.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 211.0, "general_inspection.readings.L_output_current.b": 3.8, "general_inspection.readings.L_output_current.c": 5.3, "general_inspection.readings.M_active_power.a": 0.5, "general_inspection.readings.M_active_power.b": 0.8, "general_inspection.readings.M_active_power.c": 1.2, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.5, "general_inspection.readings.O_apparent_power.b": 0.8, "general_inspection.readings.O_apparent_power.c": 1.2, "general_inspection.readings.P_output_power.a": 7.0, "general_inspection.readings.P_output_power.b": 12.0, "general_inspection.readings.P_output_power.c": 19.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.1, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.9, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.7, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 180.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 90.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 90.0, "comments_recommendation": "", "technician_name": "", "technician_id": 7222, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000446322.pdf | 4000446322 | {"station": "RAN", "date_time": "20/01/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 48.5, "general_inspection.readings.B_module_temperature.max": 32.5, "general_inspection.readings.C_battery_run_time": 150.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 282.0, "general_inspection.readings.F_battery_voltage_v.negative": 253.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 246.0, "general_inspection.readings.I_rectifier_voltage.b": 247.0, "general_inspection.readings.I_rectifier_voltage.c": 249.0, "general_inspection.readings.J_bypass_voltage.a": 282.0, "general_inspection.readings.J_bypass_voltage.b": 281.0, "general_inspection.readings.J_bypass_voltage.c": 283.0, "general_inspection.readings.K_output_voltage.a": 244.0, "general_inspection.readings.K_output_voltage.b": 242.0, "general_inspection.readings.K_output_voltage.c": 241.0, "general_inspection.readings.L_output_current.a": 0.1, "general_inspection.readings.L_output_current.b": 0.1, "general_inspection.readings.L_output_current.c": 0.2, "general_inspection.readings.M_active_power.a": 1.0, "general_inspection.readings.M_active_power.b": 1.1, "general_inspection.readings.M_active_power.c": 1.2, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.5, "general_inspection.readings.O_apparent_power.a": 0.4, "general_inspection.readings.O_apparent_power.b": 0.7, "general_inspection.readings.O_apparent_power.c": 0.6, "general_inspection.readings.P_output_power.a": 8.0, "general_inspection.readings.P_output_power.b": 1.6, "general_inspection.readings.P_output_power.c": 2.3, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.8, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.2, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.6, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 100.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 50.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 80.0, "comments_recommendation": "ok", "technician_name": "", "technician_id": 7223, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000646740.pdf | 4000646740 | {"station": "BNG", "date_time": "19/10/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 33.3, "general_inspection.readings.B_module_temperature.max": 34.2, "general_inspection.readings.C_battery_run_time": 268.8, "general_inspection.readings.D_output_frequency": 50.02, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 245.0, "general_inspection.readings.I_rectifier_voltage.b": 243.0, "general_inspection.readings.I_rectifier_voltage.c": 246.0, "general_inspection.readings.J_bypass_voltage.a": 245.0, "general_inspection.readings.J_bypass_voltage.b": 245.0, "general_inspection.readings.J_bypass_voltage.c": 246.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 2.7, "general_inspection.readings.L_output_current.b": 6.1, "general_inspection.readings.L_output_current.c": 3.9, "general_inspection.readings.M_active_power.a": 0.6, "general_inspection.readings.M_active_power.b": 1.4, "general_inspection.readings.M_active_power.c": 0.9, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.0, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 1.5, "general_inspection.readings.O_apparent_power.c": 0.8, "general_inspection.readings.P_output_power.a": 10.0, "general_inspection.readings.P_output_power.b": 22.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All equipments in a good condition.", "technician_name": "", "technician_id": 22547, "supervisor_name": "", "supervisor_id": 7262}
SC_PM_QTR_UPS_4000576113.pdf | 4000576113 | {"station": "BNG", "date_time": "19/10/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 40.3, "general_inspection.readings.B_module_temperature.max": 43.7, "general_inspection.readings.C_battery_run_time": 50.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 252.0, "general_inspection.readings.I_rectifier_voltage.b": 249.0, "general_inspection.readings.I_rectifier_voltage.c": 252.0, "general_inspection.readings.J_bypass_voltage.a": 251.0, "general_inspection.readings.J_bypass_voltage.b": 250.0, "general_inspection.readings.J_bypass_voltage.c": 253.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 3.0, "general_inspection.readings.L_output_current.b": 6.4, "general_inspection.readings.L_output_current.c": 3.7, "general_inspection.readings.M_active_power.a": 0.7, "general_inspection.readings.M_active_power.b": 1.4, "general_inspection.readings.M_active_power.c": 0.8, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.7, "general_inspection.readings.O_apparent_power.b": 1.4, "general_inspection.readings.O_apparent_power.c": 0.9, "general_inspection.readings.P_output_power.a": 10.0, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 13.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.2, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.4, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 50.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 49.0, "battery_backup_test.after.battery": 48.0, "battery_backup_test.battery_backup_time": 49.0, "comments_recommendation": "All in good condition", "technician_name": "", "technician_id": 19898, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000493756.pdf | 4000493756 | {"station": "BNG", "date_time": "19/10/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 33.2, "general_inspection.readings.B_module_temperature.max": 36.4, "general_inspection.readings.C_battery_run_time": 228.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 260.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 230.0, "general_inspection.readings.I_rectifier_voltage.b": 249.0, "general_inspection.readings.I_rectifier_voltage.c": 253.0, "general_inspection.readings.J_bypass_voltage.a": 249.0, "general_inspection.readings.J_bypass_voltage.b": 249.0, "general_inspection.readings.J_bypass_voltage.c": 254.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 2.7, "general_inspection.readings.L_output_current.b": 3.1, "general_inspection.readings.L_output_current.c": 3.8, "general_inspection.readings.M_active_power.a": 0.6, "general_inspection.readings.M_active_power.b": 1.4, "general_inspection.readings.M_active_power.c": 0.9, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.0, "general_inspection.readings.O_apparent_power.a": 5.6, "general_inspection.readings.O_apparent_power.b": 1.4, "general_inspection.readings.O_apparent_power.c": 1.8, "general_inspection.readings.P_output_power.a": 9.0, "general_inspection.readings.P_output_power.b": 22.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.4, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 150.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 70.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 70.0, "comments_recommendation": "Good Condition.", "technician_name": "", "technician_id": 7223, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000480668.pdf | 4000480668 | {"station": "BNG", "date_time": "2022-07-19T00:00:00", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 32.4, "general_inspection.readings.B_module_temperature.max": 36.4, "general_inspection.readings.C_battery_run_time": 48.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 260.0, "general_inspection.readings.F_battery_voltage_v.negative": 264.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 250.0, "general_inspection.readings.I_rectifier_voltage.b": 249.0, "general_inspection.readings.I_rectifier_voltage.c": 253.0, "general_inspection.readings.J_bypass_voltage.a": 249.0, "general_inspection.readings.J_bypass_voltage.b": 244.0, "general_inspection.readings.J_bypass_voltage.c": 253.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 2.7, "general_inspection.readings.L_output_current.b": 3.1, "general_inspection.readings.L_output_current.c": 3.8, "general_inspection.readings.M_active_power.a": 0.6, "general_inspection.readings.M_active_power.b": 1.4, "general_inspection.readings.M_active_power.c": 0.9, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.0, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 1.4, "general_inspection.readings.O_apparent_power.c": 1.8, "general_inspection.readings.P_output_power.a": 9.0, "general_inspection.readings.P_output_power.b": 22.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.1, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.4, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 150.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 70.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 70.0, "comments_recommendation": "all equitment in good condition", "technician_name": " ABDUL AZIN", "technician_id": 11727, "supervisor_name": "AZHAR YUNUS", "supervisor_id": 7111}
SC_PM_NA_UPS_NA_8.pdf |  | {"station": "BNG", "date_time": "19/07/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": null, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 31.6, "general_inspection.readings.B_module_temperature.max": 33.1, "general_inspection.readings.C_battery_run_time": 591.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 245.0, "general_inspection.readings.I_rectifier_voltage.b": 244.0, "general_inspection.readings.I_rectifier_voltage.c": 247.0, "general_inspection.readings.J_bypass_voltage.a": null, "general_inspection.readings.J_bypass_voltage.b": null, "general_inspection.readings.J_bypass_voltage.c": null, "general_inspection.readings.K_output_voltage.a": null, "general_inspection.readings.K_output_voltage.b": null, "general_inspection.readings.K_output_voltage.c": null, "general_inspection.readings.L_output_current.a": 2.7, "general_inspection.readings.L_output_current.b": 6.4, "general_inspection.readings.L_output_current.c": 3.4, "general_inspection.readings.M_active_power.a": 0.6, "general_inspection.readings.M_active_power.b": 1.5, "general_inspection.readings.M_active_power.c": 0.8, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.0, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 1.5, "general_inspection.readings.O_apparent_power.c": 1.9, "general_inspection.readings.P_output_power.a": 10.0, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 13.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "all ementien in good condition", "technician_name": "", "technician_id": 20159, "supervisor_name": "", "supervisor_id": 7256}
SC_PM_QTR_UPS_4000555042.pdf | 4000555042 | {"station": "BNG", "date_time": "19/07/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 46.0, "general_inspection.readings.B_module_temperature.max": 50.9, "general_inspection.readings.C_battery_run_time": 54.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 264.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 246.0, "general_inspection.readings.I_rectifier_voltage.b": 243.0, "general_inspection.readings.I_rectifier_voltage.c": 246.0, "general_inspection.readings.J_bypass_voltage.a": 245.0, "general_inspection.readings.J_bypass_voltage.b": 239.0, "general_inspection.readings.J_bypass_voltage.c": 240.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 2.7, "general_inspection.readings.L_output_current.b": 5.5, "general_inspection.readings.L_output_current.c": 3.5, "general_inspection.readings.M_active_power.a": 0.6, "general_inspection.readings.M_active_power.b": 1.2, "general_inspection.readings.M_active_power.c": 0.6, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 1.2, "general_inspection.readings.O_apparent_power.c": 0.8, "general_inspection.readings.P_output_power.a": 12.0, "general_inspection.readings.P_output_power.b": null, "general_inspection.readings.P_output_power.c": null, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "An equipment in good conditions", "technician_name": "", "technician_id": 7256, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000608017.pdf | 4000608017 | {"station": "BNG", "date_time": "19/04/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 31.4, "general_inspection.readings.B_module_temperature.max": 36.5, "general_inspection.readings.C_battery_run_time": 616.2, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 243.0, "general_inspection.readings.I_rectifier_voltage.b": 242.0, "general_inspection.readings.I_rectifier_voltage.c": 245.0, "general_inspection.readings.J_bypass_voltage.a": 244.0, "general_inspection.readings.J_bypass_voltage.b": 242.0, "general_inspection.readings.J_bypass_voltage.c": 246.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 2.7, "general_inspection.readings.L_output_current.b": 6.5, "general_inspection.readings.L_output_current.c": 3.9, "general_inspection.readings.M_active_power.a": 0.6, "general_inspection.readings.M_active_power.b": 0.5, "general_inspection.readings.M_active_power.c": 0.7, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.0, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 0.4, "general_inspection.readings.O_apparent_power.c": 1.7, "general_inspection.readings.P_output_power.a": 9.0, "general_inspection.readings.P_output_power.b": 22.0, "general_inspection.readings.P_output_power.c": 12.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "ADC change 2 module UPS. Bank 3 dosnt have\nbatteries. Module and all batteries in good\ncondition.", "technician_name": "", "technician_id": 19921, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000530667.pdf | 4000530667 | {"station": "BNG", "date_time": "19/04/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 46.0, "general_inspection.readings.B_module_temperature.max": 50.9, "general_inspection.readings.C_battery_run_time": 54.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 246.0, "general_inspection.readings.I_rectifier_voltage.b": 243.0, "general_inspection.readings.I_rectifier_voltage.c": 246.0, "general_inspection.readings.J_bypass_voltage.a": 245.0, "general_inspection.readings.J_bypass_voltage.b": 243.0, "general_inspection.readings.J_bypass_voltage.c": 247.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 2.7, "general_inspection.readings.L_output_current.b": 5.5, "general_inspection.readings.L_output_current.c": 3.5, "general_inspection.readings.M_active_power.a": 0.6, "general_inspection.readings.M_active_power.b": 1.2, "general_inspection.readings.M_active_power.c": 0.7, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 1.2, "general_inspection.readings.O_apparent_power.c": 0.8, "general_inspection.readings.P_output_power.a": 10.0, "general_inspection.readings.P_output_power.b": 101.0, "general_inspection.readings.P_output_power.c": 12.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.8, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.9, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 55.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 25.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 55.0, "comments_recommendation": "all equipment in good conditions", "technician_name": "", "technician_id": 11727, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000467069.pdf | 4000467069 | {"station": "BNG", "date_time": "19/04/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 220.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 270.0, "general_inspection.readings.F_battery_voltage_v.negative": 270.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 249.0, "general_inspection.readings.I_rectifier_voltage.b": 246.0, "general_inspection.readings.I_rectifier_voltage.c": 249.0, "general_inspection.readings.J_bypass_voltage.a": 248.0, "general_inspection.readings.J_bypass_voltage.b": 247.0, "general_inspection.readings.J_bypass_voltage.c": 230.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 2.7, "general_inspection.readings.L_output_current.b": 4.8, "general_inspection.readings.L_output_current.c": 3.9, "general_inspection.readings.M_active_power.a": 0.6, "general_inspection.readings.M_active_power.b": 0.6, "general_inspection.readings.M_active_power.c": 1.0, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.0, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 1.1, "general_inspection.readings.O_apparent_power.c": 1.0, "general_inspection.readings.P_output_power.a": 10.0, "general_inspection.readings.P_output_power.b": 16.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.7, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.6, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 100.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 50.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 90.0, "comments_recommendation": "2 battery bank faulty", "technician_name": "", "technician_id": 7110, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000660374.pdf | 4000660374 | {"station": "BNG", "date_time": "19/01/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 31.2, "general_inspection.readings.B_module_temperature.max": 31.9, "general_inspection.readings.C_battery_run_time": 606.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 249.0, "general_inspection.readings.I_rectifier_voltage.b": 247.0, "general_inspection.readings.I_rectifier_voltage.c": 251.0, "general_inspection.readings.J_bypass_voltage.a": 249.0, "general_inspection.readings.J_bypass_voltage.b": 247.0, "general_inspection.readings.J_bypass_voltage.c": 251.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 2.8, "general_inspection.readings.L_output_current.b": 6.2, "general_inspection.readings.L_output_current.c": 3.6, "general_inspection.readings.M_active_power.a": 0.6, "general_inspection.readings.M_active_power.b": 1.4, "general_inspection.readings.M_active_power.c": 1.0, "general_inspection.readings.N_reactive_power.a": 0.2, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 1.4, "general_inspection.readings.O_apparent_power.c": 0.8, "general_inspection.readings.P_output_power.a": 10.0, "general_inspection.readings.P_output_power.b": 22.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All equipment in a good condition.", "technician_name": "", "technician_id": "22775", "supervisor_name": "", "supervisor_id": "7110"}
SC_PM_QTR_UPS_4000597708.pdf | 4000597708 | {"station": "BNG", "date_time": "19/01/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 32.8, "general_inspection.readings.B_module_temperature.max": 35.7, "general_inspection.readings.C_battery_run_time": 53.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 248.0, "general_inspection.readings.I_rectifier_voltage.b": 246.0, "general_inspection.readings.I_rectifier_voltage.c": 250.0, "general_inspection.readings.J_bypass_voltage.a": 247.0, "general_inspection.readings.J_bypass_voltage.b": 246.0, "general_inspection.readings.J_bypass_voltage.c": 250.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 3.0, "general_inspection.readings.L_output_current.b": 6.6, "general_inspection.readings.L_output_current.c": 4.0, "general_inspection.readings.M_active_power.a": 0.7, "general_inspection.readings.M_active_power.b": 1.6, "general_inspection.readings.M_active_power.c": 0.9, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.0, "general_inspection.readings.O_apparent_power.a": 0.7, "general_inspection.readings.O_apparent_power.b": 1.6, "general_inspection.readings.O_apparent_power.c": 1.0, "general_inspection.readings.P_output_power.a": 11.0, "general_inspection.readings.P_output_power.b": 24.0, "general_inspection.readings.P_output_power.c": 15.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "Module need to calibrate.\n All battery in good condition.", "technician_name": "", "technician_id": 20452, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000509121.pdf | 4000509121 | {"station": "BNG", "date_time": "19/01/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 33.1, "general_inspection.readings.B_module_temperature.max": 36.4, "general_inspection.readings.C_battery_run_time": 220.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 260.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 230.0, "general_inspection.readings.I_rectifier_voltage.b": 249.0, "general_inspection.readings.I_rectifier_voltage.c": 253.0, "general_inspection.readings.J_bypass_voltage.a": 249.0, "general_inspection.readings.J_bypass_voltage.b": 249.0, "general_inspection.readings.J_bypass_voltage.c": 254.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 2.7, "general_inspection.readings.L_output_current.b": 3.1, "general_inspection.readings.L_output_current.c": 3.8, "general_inspection.readings.M_active_power.a": 0.6, "general_inspection.readings.M_active_power.b": 1.4, "general_inspection.readings.M_active_power.c": 0.9, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.0, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 1.4, "general_inspection.readings.O_apparent_power.c": 1.8, "general_inspection.readings.P_output_power.a": 9.0, "general_inspection.readings.P_output_power.b": 22.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.2, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 150.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 75.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 75.0, "comments_recommendation": "", "technician_name": "", "technician_id": 7222, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000446363.pdf | 4000446363 | {"station": "BNG", "date_time": "19/01/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 45.8, "general_inspection.readings.B_module_temperature.max": 50.7, "general_inspection.readings.C_battery_run_time": 220.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 270.0, "general_inspection.readings.F_battery_voltage_v.negative": 270.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 249.0, "general_inspection.readings.I_rectifier_voltage.b": 296.0, "general_inspection.readings.I_rectifier_voltage.c": 249.0, "general_inspection.readings.J_bypass_voltage.a": 248.0, "general_inspection.readings.J_bypass_voltage.b": 247.0, "general_inspection.readings.J_bypass_voltage.c": 280.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 2.7, "general_inspection.readings.L_output_current.b": 4.8, "general_inspection.readings.L_output_current.c": 3.9, "general_inspection.readings.M_active_power.a": 0.6, "general_inspection.readings.M_active_power.b": 0.6, "general_inspection.readings.M_active_power.c": 1.0, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.0, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 1.1, "general_inspection.readings.O_apparent_power.c": 1.0, "general_inspection.readings.P_output_power.a": 10.0, "general_inspection.readings.P_output_power.b": 16.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.7, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.8, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 80.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 40.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 40.0, "comments_recommendation": "2 battery book faulty", "technician_name": "", "technician_id": 7222, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000644023.pdf | 4000644023 | {"station": "IBI", "date_time": "18/10/2024 ", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 36.0, "general_inspection.readings.B_module_temperature.max": 42.7, "general_inspection.readings.C_battery_run_time": 123.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 245.0, "general_inspection.readings.I_rectifier_voltage.b": 245.0, "general_inspection.readings.I_rectifier_voltage.c": 248.0, "general_inspection.readings.J_bypass_voltage.a": 245.0, "general_inspection.readings.J_bypass_voltage.b": 245.0, "general_inspection.readings.J_bypass_voltage.c": 247.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 2.9, "general_inspection.readings.L_output_current.b": 7.1, "general_inspection.readings.L_output_current.c": 10.4, "general_inspection.readings.M_active_power.a": 0.6, "general_inspection.readings.M_active_power.b": 1.4, "general_inspection.readings.M_active_power.c": 2.4, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.5, "general_inspection.readings.N_reactive_power.c": 0.5, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 1.6, "general_inspection.readings.O_apparent_power.c": 2.5, "general_inspection.readings.P_output_power.a": 10.0, "general_inspection.readings.P_output_power.b": 25.0, "general_inspection.readings.P_output_power.c": 38.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All equipments in a good condition.", "technician_name": "", "technician_id": 22547, "supervisor_name": "", "supervisor_id": 7262}
SC_PM_QTR_UPS_4000576144.pdf | 4000576144 | {"station": "IBI", "date_time": "18/10/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 30.0, "general_inspection.readings.B_module_temperature.max": 35.4, "general_inspection.readings.C_battery_run_time": 120.0, "general_inspection.readings.D_output_frequency": 50.02, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 233.0, "general_inspection.readings.F_battery_voltage_v.negative": 273.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 252.0, "general_inspection.readings.I_rectifier_voltage.b": 252.0, "general_inspection.readings.I_rectifier_voltage.c": 256.0, "general_inspection.readings.J_bypass_voltage.a": 252.0, "general_inspection.readings.J_bypass_voltage.b": 252.0, "general_inspection.readings.J_bypass_voltage.c": 254.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 2.9, "general_inspection.readings.L_output_current.b": 6.7, "general_inspection.readings.L_output_current.c": 11.3, "general_inspection.readings.M_active_power.a": 0.7, "general_inspection.readings.M_active_power.b": 1.3, "general_inspection.readings.M_active_power.c": 2.6, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.5, "general_inspection.readings.N_reactive_power.c": 0.5, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 1.7, "general_inspection.readings.O_apparent_power.c": 2.7, "general_inspection.readings.P_output_power.a": 22.0, "general_inspection.readings.P_output_power.b": 32.0, "general_inspection.readings.P_output_power.c": 40.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.3, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.4, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": "", "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": null, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": null, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": null, "servicing_and_cleaning.normalized_all_battery_breakers.status": null, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": null, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": null, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": null, "servicing_and_cleaning.check_everything__normal.status": null, "battery_backup_test.check_battery_level.status": null, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": null, "battery_backup_test.turn_off_main_switch_breaker.status": null, "battery_backup_test.confirm_alarm_sounding.status": null, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": null, "battery_backup_test.switch_on_back_main_switch_breaker.status": null, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "Slave module faulty only \n use 1 bank batteries", "technician_name": "", "technician_id": "19898", "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000493774.pdf | 4000493774 | {"station": "IBI", "date_time": "18/10/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 36.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 138.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 236.0, "general_inspection.readings.F_battery_voltage_v.negative": 236.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 250.0, "general_inspection.readings.I_rectifier_voltage.b": 250.0, "general_inspection.readings.I_rectifier_voltage.c": 251.0, "general_inspection.readings.J_bypass_voltage.a": 250.0, "general_inspection.readings.J_bypass_voltage.b": 250.0, "general_inspection.readings.J_bypass_voltage.c": 252.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 3.2, "general_inspection.readings.L_output_current.b": 6.9, "general_inspection.readings.L_output_current.c": 7.7, "general_inspection.readings.M_active_power.a": 0.7, "general_inspection.readings.M_active_power.b": 1.5, "general_inspection.readings.M_active_power.c": 2.0, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.4, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.7, "general_inspection.readings.O_apparent_power.b": 1.6, "general_inspection.readings.O_apparent_power.c": 1.9, "general_inspection.readings.P_output_power.a": 11.0, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 29.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.8, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.9, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 186.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 80.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "", "technician_name": "", "technician_id": 7222, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_NA_UPS_NA_5.pdf |  | {"station": "IBI", "date_time": "18/07/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": null, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 40.7, "general_inspection.readings.B_module_temperature.max": 48.1, "general_inspection.readings.C_battery_run_time": 111.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 242.0, "general_inspection.readings.I_rectifier_voltage.b": 242.0, "general_inspection.readings.I_rectifier_voltage.c": 245.0, "general_inspection.readings.J_bypass_voltage.a": 242.0, "general_inspection.readings.J_bypass_voltage.b": 242.0, "general_inspection.readings.J_bypass_voltage.c": 244.0, "general_inspection.readings.K_output_voltage.a": null, "general_inspection.readings.K_output_voltage.b": null, "general_inspection.readings.K_output_voltage.c": null, "general_inspection.readings.L_output_current.a": 2.9, "general_inspection.readings.L_output_current.b": 7.0, "general_inspection.readings.L_output_current.c": 10.7, "general_inspection.readings.M_active_power.a": 0.6, "general_inspection.readings.M_active_power.b": 1.4, "general_inspection.readings.M_active_power.c": 2.6, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.5, "general_inspection.readings.N_reactive_power.c": 0.5, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 1.7, "general_inspection.readings.O_apparent_power.c": 2.6, "general_inspection.readings.P_output_power.a": 10.0, "general_inspection.readings.P_output_power.b": 27.0, "general_inspection.readings.P_output_power.c": 39.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "UPS in good condition.", "technician_name": "", "technician_id": 20159, "supervisor_name": "", "supervisor_id": 7256}
SC_PM_QTR_UPS_4000555072.pdf | 4000555072 | {"station": "IBI", "date_time": "18/07/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 46.0, "general_inspection.readings.B_module_temperature.max": 50.9, "general_inspection.readings.C_battery_run_time": 54.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 246.0, "general_inspection.readings.I_rectifier_voltage.b": 243.0, "general_inspection.readings.I_rectifier_voltage.c": 246.0, "general_inspection.readings.J_bypass_voltage.a": 245.0, "general_inspection.readings.J_bypass_voltage.b": 243.0, "general_inspection.readings.J_bypass_voltage.c": 247.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 2.7, "general_inspection.readings.L_output_current.b": 5.5, "general_inspection.readings.L_output_current.c": 3.5, "general_inspection.readings.M_active_power.a": 0.6, "general_inspection.readings.M_active_power.b": 1.2, "general_inspection.readings.M_active_power.c": 0.7, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 1.2, "general_inspection.readings.O_apparent_power.c": 0.8, "general_inspection.readings.P_output_power.a": 10.0, "general_inspection.readings.P_output_power.b": 19.0, "general_inspection.readings.P_output_power.c": 12.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "all equipment in good condition.", "technician_name": "", "technician_id": 7256, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000480689.pdf | 4000480689 | {"station": "IBI", "date_time": "18/07/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 36.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 129.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 286.0, "general_inspection.readings.F_battery_voltage_v.negative": 286.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 250.0, "general_inspection.readings.I_rectifier_voltage.b": 250.0, "general_inspection.readings.I_rectifier_voltage.c": 254.0, "general_inspection.readings.J_bypass_voltage.a": 250.0, "general_inspection.readings.J_bypass_voltage.b": 250.0, "general_inspection.readings.J_bypass_voltage.c": 252.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 3.2, "general_inspection.readings.L_output_current.b": 6.9, "general_inspection.readings.L_output_current.c": 7.7, "general_inspection.readings.M_active_power.a": 0.7, "general_inspection.readings.M_active_power.b": 1.5, "general_inspection.readings.M_active_power.c": 2.0, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.4, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.7, "general_inspection.readings.O_apparent_power.b": 1.6, "general_inspection.readings.O_apparent_power.c": 1.9, "general_inspection.readings.P_output_power.a": 11.0, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 29.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.8, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.7, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 190.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 80.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 80.0, "comments_recommendation": "ok", "technician_name": "ROHIZAN", "technician_id": 7223, "supervisor_name": "AZHAR YUNUS", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000608042.pdf | 4000608042 | {"station": "IBI", "date_time": "18/04/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 120.0, "general_inspection.readings.D_output_frequency": 50.04, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 269.0, "general_inspection.readings.F_battery_voltage_v.negative": 269.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 251.0, "general_inspection.readings.I_rectifier_voltage.b": 251.0, "general_inspection.readings.I_rectifier_voltage.c": 255.0, "general_inspection.readings.J_bypass_voltage.a": 251.0, "general_inspection.readings.J_bypass_voltage.b": 251.0, "general_inspection.readings.J_bypass_voltage.c": 252.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 2.9, "general_inspection.readings.L_output_current.b": 6.5, "general_inspection.readings.L_output_current.c": 10.8, "general_inspection.readings.M_active_power.a": 0.7, "general_inspection.readings.M_active_power.b": 1.4, "general_inspection.readings.M_active_power.c": 2.6, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.5, "general_inspection.readings.N_reactive_power.c": 0.4, "general_inspection.readings.O_apparent_power.a": 0.7, "general_inspection.readings.O_apparent_power.b": 1.6, "general_inspection.readings.O_apparent_power.c": 2.5, "general_inspection.readings.P_output_power.a": 11.0, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 38.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "Equipment is in good condition. Battery bank 2 no batery (C and D)", "technician_name": "", "technician_id": 20449, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000530683.pdf | 4000530683 | {"station": "IBI", "date_time": "18/04/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 37.7, "general_inspection.readings.B_module_temperature.max": 44.7, "general_inspection.readings.C_battery_run_time": 122.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 268.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 252.0, "general_inspection.readings.I_rectifier_voltage.b": 253.0, "general_inspection.readings.I_rectifier_voltage.c": 256.0, "general_inspection.readings.J_bypass_voltage.a": 253.0, "general_inspection.readings.J_bypass_voltage.b": 253.0, "general_inspection.readings.J_bypass_voltage.c": 254.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 2.7, "general_inspection.readings.L_output_current.b": 6.2, "general_inspection.readings.L_output_current.c": 11.4, "general_inspection.readings.M_active_power.a": 0.6, "general_inspection.readings.M_active_power.b": 1.4, "general_inspection.readings.M_active_power.c": 2.6, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.5, "general_inspection.readings.N_reactive_power.c": 0.5, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 1.4, "general_inspection.readings.O_apparent_power.c": 2.7, "general_inspection.readings.P_output_power.a": 9.0, "general_inspection.readings.P_output_power.b": 22.0, "general_inspection.readings.P_output_power.c": 41.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.2, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.8, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.0, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 150.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 100.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 180.0, "comments_recommendation": "all equitment in good conditions \n #1 unit bateri bank not good condition \n 1 unit module faulty", "technician_name": "", "technician_id": 11727, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000467087.pdf | 4000467087 | {"station": "IBI", "date_time": "18/04/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": null, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 36.4, "general_inspection.readings.B_module_temperature.max": 44.4, "general_inspection.readings.C_battery_run_time": 137.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 206.0, "general_inspection.readings.F_battery_voltage_v.negative": 286.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 250.0, "general_inspection.readings.I_rectifier_voltage.b": 250.0, "general_inspection.readings.I_rectifier_voltage.c": 254.0, "general_inspection.readings.J_bypass_voltage.a": 250.0, "general_inspection.readings.J_bypass_voltage.b": 250.0, "general_inspection.readings.J_bypass_voltage.c": 254.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 259.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 3.2, "general_inspection.readings.L_output_current.b": 6.9, "general_inspection.readings.L_output_current.c": 7.4, "general_inspection.readings.M_active_power.a": 0.7, "general_inspection.readings.M_active_power.b": 1.5, "general_inspection.readings.M_active_power.c": 2.0, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.4, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.7, "general_inspection.readings.O_apparent_power.b": 1.6, "general_inspection.readings.O_apparent_power.c": 1.9, "general_inspection.readings.P_output_power.a": 11.0, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 29.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.7, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 150.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 80.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 150.0, "comments_recommendation": "OK", "technician_name": "", "technician_id": 7110, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000669108.pdf | 4000669108 | {"station": "IBI", "date_time": "18/01/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": null, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 31.5, "general_inspection.readings.B_module_temperature.max": 35.2, "general_inspection.readings.C_battery_run_time": 121.8, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 266.0, "general_inspection.readings.F_battery_voltage_v.negative": 266.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 243.0, "general_inspection.readings.I_rectifier_voltage.b": 243.0, "general_inspection.readings.I_rectifier_voltage.c": 246.0, "general_inspection.readings.J_bypass_voltage.a": 243.0, "general_inspection.readings.J_bypass_voltage.b": 243.0, "general_inspection.readings.J_bypass_voltage.c": 245.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 2.9, "general_inspection.readings.L_output_current.b": 6.8, "general_inspection.readings.L_output_current.c": 4.7, "general_inspection.readings.M_active_power.a": 0.6, "general_inspection.readings.M_active_power.b": 1.5, "general_inspection.readings.M_active_power.c": 2.5, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.6, "general_inspection.readings.N_reactive_power.c": 0.5, "general_inspection.readings.O_apparent_power.a": 0.7, "general_inspection.readings.O_apparent_power.b": 1.7, "general_inspection.readings.O_apparent_power.c": 2.5, "general_inspection.readings.P_output_power.a": 10.0, "general_inspection.readings.P_output_power.b": 25.0, "general_inspection.readings.P_output_power.c": 36.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All equipment in a good condition", "technician_name": "", "technician_id": 22775, "supervisor_name": "", "supervisor_id": 7110}
SC_PM_QTR_UPS_4000597779.pdf | 4000597779 | {"station": "IBI", "date_time": "18/01/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 31.5, "general_inspection.readings.B_module_temperature.max": 38.1, "general_inspection.readings.C_battery_run_time": 120.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 268.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 245.0, "general_inspection.readings.I_rectifier_voltage.b": 246.0, "general_inspection.readings.I_rectifier_voltage.c": 249.0, "general_inspection.readings.J_bypass_voltage.a": 245.0, "general_inspection.readings.J_bypass_voltage.b": 246.0, "general_inspection.readings.J_bypass_voltage.c": 248.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 3.2, "general_inspection.readings.L_output_current.b": 6.5, "general_inspection.readings.L_output_current.c": 10.7, "general_inspection.readings.M_active_power.a": 0.7, "general_inspection.readings.M_active_power.b": 1.4, "general_inspection.readings.M_active_power.c": 2.5, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.5, "general_inspection.readings.N_reactive_power.c": 0.5, "general_inspection.readings.O_apparent_power.a": 0.7, "general_inspection.readings.O_apparent_power.b": 1.6, "general_inspection.readings.O_apparent_power.c": 2.5, "general_inspection.readings.P_output_power.a": 11.0, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 38.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "-Module P2 notified alarm Phase Fault\n-there are serval Faulty battery burn\n-beside that hardware in good condition\n- Bank 1 and 2 kembung", "technician_name": "", "technician_id": 20079, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000509107.pdf | 4000509107 | {"station": "IBI", "date_time": "18/01/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 36.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 190.0, "general_inspection.readings.D_output_frequency": 60.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 286.0, "general_inspection.readings.F_battery_voltage_v.negative": 286.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 250.0, "general_inspection.readings.I_rectifier_voltage.b": 250.0, "general_inspection.readings.I_rectifier_voltage.c": 254.0, "general_inspection.readings.J_bypass_voltage.a": 250.0, "general_inspection.readings.J_bypass_voltage.b": 250.0, "general_inspection.readings.J_bypass_voltage.c": 254.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 3.2, "general_inspection.readings.L_output_current.b": 6.4, "general_inspection.readings.L_output_current.c": 7.1, "general_inspection.readings.M_active_power.a": 0.4, "general_inspection.readings.M_active_power.b": 1.5, "general_inspection.readings.M_active_power.c": 2.0, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.4, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.7, "general_inspection.readings.O_apparent_power.b": 1.6, "general_inspection.readings.O_apparent_power.c": 1.9, "general_inspection.readings.P_output_power.a": 11.0, "general_inspection.readings.P_output_power.b": 24.0, "general_inspection.readings.P_output_power.c": 30.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.8, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.9, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.7, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 140.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 95.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 95.0, "comments_recommendation": "All equipment in good condition.", "technician_name": "YARUL AZWAN", "technician_id": 7110, "supervisor_name": "", "supervisor_id": " "}
SC_PM_QTR_UPS_4000446346.pdf | 4000446346 | {"station": "IBI", "date_time": "18/01/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 36.4, "general_inspection.readings.B_module_temperature.max": 44.4, "general_inspection.readings.C_battery_run_time": 137.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 286.0, "general_inspection.readings.F_battery_voltage_v.negative": 286.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 280.0, "general_inspection.readings.I_rectifier_voltage.b": 250.0, "general_inspection.readings.I_rectifier_voltage.c": 254.0, "general_inspection.readings.J_bypass_voltage.a": 280.0, "general_inspection.readings.J_bypass_voltage.b": 250.0, "general_inspection.readings.J_bypass_voltage.c": 254.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 3.2, "general_inspection.readings.L_output_current.b": 6.9, "general_inspection.readings.L_output_current.c": 7.7, "general_inspection.readings.M_active_power.a": 0.7, "general_inspection.readings.M_active_power.b": 1.5, "general_inspection.readings.M_active_power.c": 2.0, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.4, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.7, "general_inspection.readings.O_apparent_power.b": 1.6, "general_inspection.readings.O_apparent_power.c": 1.9, "general_inspection.readings.P_output_power.a": 11.0, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 29.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.8, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.7, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 160.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 80.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 80.0, "comments_recommendation": "ok", "technician_name": "", "technician_id": 7222, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000576134.pdf | 4000576134 | {"station": "HAH", "date_time": "17/10/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 33.3, "general_inspection.readings.B_module_temperature.max": 38.8, "general_inspection.readings.C_battery_run_time": 233.0, "general_inspection.readings.D_output_frequency": 50.5, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.1, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 238.0, "general_inspection.readings.I_rectifier_voltage.b": 238.0, "general_inspection.readings.I_rectifier_voltage.c": 240.0, "general_inspection.readings.J_bypass_voltage.a": 236.0, "general_inspection.readings.J_bypass_voltage.b": 237.0, "general_inspection.readings.J_bypass_voltage.c": 240.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 246.0, "general_inspection.readings.L_output_current.a": 1.5, "general_inspection.readings.L_output_current.b": 6.3, "general_inspection.readings.L_output_current.c": 3.4, "general_inspection.readings.M_active_power.a": 0.4, "general_inspection.readings.M_active_power.b": 1.4, "general_inspection.readings.M_active_power.c": 0.7, "general_inspection.readings.N_reactive_power.a": 1.0, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.4, "general_inspection.readings.O_apparent_power.b": 1.4, "general_inspection.readings.O_apparent_power.c": 0.7, "general_inspection.readings.P_output_power.a": 6.0, "general_inspection.readings.P_output_power.b": 22.0, "general_inspection.readings.P_output_power.c": 10.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "all equipment in good conditiong", "technician_name": "", "technician_id": 7256, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000493769.pdf | 4000493769 | {"station": "HAH", "date_time": "17/10/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 36.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 372.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 271.0, "general_inspection.readings.F_battery_voltage_v.negative": 271.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 237.0, "general_inspection.readings.I_rectifier_voltage.b": 236.0, "general_inspection.readings.I_rectifier_voltage.c": 239.0, "general_inspection.readings.J_bypass_voltage.a": 238.0, "general_inspection.readings.J_bypass_voltage.b": 236.0, "general_inspection.readings.J_bypass_voltage.c": 239.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.4, "general_inspection.readings.L_output_current.b": 2.3, "general_inspection.readings.L_output_current.c": 2.7, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.5, "general_inspection.readings.M_active_power.c": 0.6, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.5, "general_inspection.readings.O_apparent_power.c": 0.6, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 8.0, "general_inspection.readings.P_output_power.c": 9.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.5, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.5, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 180.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 90.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 90.0, "comments_recommendation": "", "technician_name": "", "technician_id": "7222", "supervisor_name": "", "supervisor_id": "7111"}
SC_PM_QTR_UPS_4000646788.pdf | 4000646788 | {"station": "HAH", "date_time": "17/10/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 321.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 240.0, "general_inspection.readings.I_rectifier_voltage.b": 239.0, "general_inspection.readings.I_rectifier_voltage.c": 242.0, "general_inspection.readings.J_bypass_voltage.a": 239.0, "general_inspection.readings.J_bypass_voltage.b": 238.0, "general_inspection.readings.J_bypass_voltage.c": 242.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.5, "general_inspection.readings.L_output_current.b": 3.6, "general_inspection.readings.L_output_current.c": 2.9, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.8, "general_inspection.readings.M_active_power.c": 0.6, "general_inspection.readings.N_reactive_power.a": 10.0, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.8, "general_inspection.readings.O_apparent_power.c": 0.6, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 12.0, "general_inspection.readings.P_output_power.c": 9.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All equipment in a good condition.", "technician_name": "", "technician_id": 20858, "supervisor_name": "", "supervisor_id": 7262}
SC_PM_NA_UPS_NA_6.pdf |  | {"station": "HAH", "date_time": "17/07/7024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 37.1, "general_inspection.readings.B_module_temperature.max": 42.9, "general_inspection.readings.C_battery_run_time": 315.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 241.0, "general_inspection.readings.I_rectifier_voltage.b": 239.0, "general_inspection.readings.I_rectifier_voltage.c": 242.0, "general_inspection.readings.J_bypass_voltage.a": 241.0, "general_inspection.readings.J_bypass_voltage.b": 239.0, "general_inspection.readings.J_bypass_voltage.c": 241.0, "general_inspection.readings.K_output_voltage.a": null, "general_inspection.readings.K_output_voltage.b": null, "general_inspection.readings.K_output_voltage.c": null, "general_inspection.readings.L_output_current.a": 1.6, "general_inspection.readings.L_output_current.b": 3.5, "general_inspection.readings.L_output_current.c": 3.4, "general_inspection.readings.M_active_power.a": 0.4, "general_inspection.readings.M_active_power.b": 0.8, "general_inspection.readings.M_active_power.c": 0.7, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.0, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.8, "general_inspection.readings.O_apparent_power.c": 0.7, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 13.0, "general_inspection.readings.P_output_power.c": 10.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All equipment in good condition.", "technician_name": "", "technician_id": 19920, "supervisor_name": "", "supervisor_id": 7256}
SC_PM_QTR_UPS_4000555066.pdf | 4000555066 | {"station": "HAH", "date_time": "17/07/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 33.9, "general_inspection.readings.B_module_temperature.max": 39.9, "general_inspection.readings.C_battery_run_time": 280.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.1, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 237.0, "general_inspection.readings.I_rectifier_voltage.b": 236.0, "general_inspection.readings.I_rectifier_voltage.c": 239.0, "general_inspection.readings.J_bypass_voltage.a": 238.0, "general_inspection.readings.J_bypass_voltage.b": 236.0, "general_inspection.readings.J_bypass_voltage.c": 239.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.6, "general_inspection.readings.L_output_current.b": 3.6, "general_inspection.readings.L_output_current.c": 2.8, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.7, "general_inspection.readings.M_active_power.c": 0.8, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.0, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.8, "general_inspection.readings.O_apparent_power.c": 0.8, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 13.0, "general_inspection.readings.P_output_power.c": 12.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "all equipment in good condition", "technician_name": "", "technician_id": 7256, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000480684.pdf | 4000480684 | {"station": "HAH", "date_time": "17/07/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 36.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 380.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 271.0, "general_inspection.readings.F_battery_voltage_v.negative": 271.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 237.0, "general_inspection.readings.I_rectifier_voltage.b": 236.0, "general_inspection.readings.I_rectifier_voltage.c": 239.0, "general_inspection.readings.J_bypass_voltage.a": 237.0, "general_inspection.readings.J_bypass_voltage.b": 236.0, "general_inspection.readings.J_bypass_voltage.c": 239.0, "general_inspection.readings.K_output_voltage.a": 238.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 1.4, "general_inspection.readings.L_output_current.b": 2.3, "general_inspection.readings.L_output_current.c": 2.7, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.5, "general_inspection.readings.M_active_power.c": 0.6, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.5, "general_inspection.readings.O_apparent_power.c": 0.6, "general_inspection.readings.P_output_power.a": 8.0, "general_inspection.readings.P_output_power.b": 8.0, "general_inspection.readings.P_output_power.c": 9.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.5, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.8, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 170.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 90.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 90.0, "comments_recommendation": "", "technician_name": "ROHIZAN", "technician_id": 7223, "supervisor_name": "AZHAR YUNUS", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000608037.pdf | 4000608037 | {"station": "HAH", "date_time": "17/04/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 254.0, "general_inspection.readings.D_output_frequency": 50.5, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.1, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 239.0, "general_inspection.readings.I_rectifier_voltage.b": 237.0, "general_inspection.readings.I_rectifier_voltage.c": 240.0, "general_inspection.readings.J_bypass_voltage.a": 238.0, "general_inspection.readings.J_bypass_voltage.b": 237.0, "general_inspection.readings.J_bypass_voltage.c": 240.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.6, "general_inspection.readings.L_output_current.b": 3.5, "general_inspection.readings.L_output_current.c": 3.7, "general_inspection.readings.M_active_power.a": 0.4, "general_inspection.readings.M_active_power.b": 0.8, "general_inspection.readings.M_active_power.c": 0.7, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.0, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.9, "general_inspection.readings.O_apparent_power.c": 0.7, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 12.0, "general_inspection.readings.P_output_power.c": 11.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "Bank 1 & Bank 2 dismantle further maintenance", "technician_name": "", "technician_id": 20449, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000530679.pdf | 4000530679 | {"station": "HAH", "date_time": "17/04/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 36.9, "general_inspection.readings.B_module_temperature.max": 43.0, "general_inspection.readings.C_battery_run_time": 240.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 239.0, "general_inspection.readings.I_rectifier_voltage.b": 237.0, "general_inspection.readings.I_rectifier_voltage.c": 239.0, "general_inspection.readings.J_bypass_voltage.a": 238.0, "general_inspection.readings.J_bypass_voltage.b": 237.0, "general_inspection.readings.J_bypass_voltage.c": 240.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.6, "general_inspection.readings.L_output_current.b": 6.1, "general_inspection.readings.L_output_current.c": 2.6, "general_inspection.readings.M_active_power.a": 0.4, "general_inspection.readings.M_active_power.b": 1.3, "general_inspection.readings.M_active_power.c": 0.7, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.4, "general_inspection.readings.O_apparent_power.b": 1.4, "general_inspection.readings.O_apparent_power.c": 0.6, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 21.0, "general_inspection.readings.P_output_power.c": 9.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.8, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.2, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.1, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 150.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 150.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 180.0, "comments_recommendation": "all equipment", "technician_name": "", "technician_id": 11727, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000467082.pdf | 4000467082 | {"station": "HAH", "date_time": "17/04/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 37.9, "general_inspection.readings.B_module_temperature.max": 58.9, "general_inspection.readings.C_battery_run_time": 326.0, "general_inspection.readings.D_output_frequency": 50.06, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 271.0, "general_inspection.readings.F_battery_voltage_v.negative": 271.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 238.0, "general_inspection.readings.I_rectifier_voltage.b": 237.0, "general_inspection.readings.I_rectifier_voltage.c": 240.0, "general_inspection.readings.J_bypass_voltage.a": 238.0, "general_inspection.readings.J_bypass_voltage.b": 237.0, "general_inspection.readings.J_bypass_voltage.c": 24.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.3, "general_inspection.readings.L_output_current.b": 3.8, "general_inspection.readings.L_output_current.c": 2.6, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.8, "general_inspection.readings.M_active_power.c": 0.6, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.9, "general_inspection.readings.O_apparent_power.c": 0.6, "general_inspection.readings.P_output_power.a": 4.0, "general_inspection.readings.P_output_power.b": 15.0, "general_inspection.readings.P_output_power.c": 9.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.4, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 150.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 80.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 80.0, "comments_recommendation": "all equitment in good conditions", "technician_name": "", "technician_id": "11727", "supervisor_name": "", "supervisor_id": "7111"}
SC_PM_QTR_UPS_4000669114.pdf | 4000669114 | {"station": "HAH", "date_time": "17/01/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 30.8, "general_inspection.readings.B_module_temperature.max": 34.7, "general_inspection.readings.C_battery_run_time": 273.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 26.7, "general_inspection.readings.F_battery_voltage_v.negative": 26.7, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 235.0, "general_inspection.readings.I_rectifier_voltage.b": 234.0, "general_inspection.readings.I_rectifier_voltage.c": 236.0, "general_inspection.readings.J_bypass_voltage.a": 235.0, "general_inspection.readings.J_bypass_voltage.b": 234.0, "general_inspection.readings.J_bypass_voltage.c": 239.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.4, "general_inspection.readings.L_output_current.b": 3.8, "general_inspection.readings.L_output_current.c": 2.6, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.8, "general_inspection.readings.M_active_power.c": 0.6, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.9, "general_inspection.readings.O_apparent_power.c": 0.6, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 13.0, "general_inspection.readings.P_output_power.c": 10.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All battery and module working properly without any error.\nBank 1 and 2 not available. Only bank 3 is available and in good condition", "technician_name": "", "technician_id": 22775, "supervisor_name": "", "supervisor_id": 7110}
SC_PM_QTR_UPS_4000597748.pdf | 4000597748 | {"station": "HAH", "date_time": "17/01/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 35.7, "general_inspection.readings.B_module_temperature.max": 41.5, "general_inspection.readings.C_battery_run_time": 330.0, "general_inspection.readings.D_output_frequency": 50.04, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.1, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 240.0, "general_inspection.readings.I_rectifier_voltage.b": 237.0, "general_inspection.readings.I_rectifier_voltage.c": 240.0, "general_inspection.readings.J_bypass_voltage.a": 238.0, "general_inspection.readings.J_bypass_voltage.b": 237.0, "general_inspection.readings.J_bypass_voltage.c": 240.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.5, "general_inspection.readings.L_output_current.b": 3.5, "general_inspection.readings.L_output_current.c": 3.0, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.8, "general_inspection.readings.M_active_power.c": 0.7, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.0, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.8, "general_inspection.readings.O_apparent_power.c": 0.7, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 13.0, "general_inspection.readings.P_output_power.c": 10.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "* all battery fault except bank F.\n* condition both module in good condition.\n* battery take out. except bank F", "technician_name": "", "technician_id": 19898, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000509110.pdf | 4000509110 | {"station": "HAH", "date_time": "17/01/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 24.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 126.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 277.0, "general_inspection.readings.F_battery_voltage_v.negative": 271.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 255.0, "general_inspection.readings.I_rectifier_voltage.b": 254.0, "general_inspection.readings.I_rectifier_voltage.c": 256.0, "general_inspection.readings.J_bypass_voltage.a": 255.0, "general_inspection.readings.J_bypass_voltage.b": 254.0, "general_inspection.readings.J_bypass_voltage.c": 256.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 3.2, "general_inspection.readings.L_output_current.b": 6.3, "general_inspection.readings.L_output_current.c": 7.6, "general_inspection.readings.M_active_power.a": 0.7, "general_inspection.readings.M_active_power.b": 1.5, "general_inspection.readings.M_active_power.c": 1.8, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.3, "general_inspection.readings.N_reactive_power.c": 0.5, "general_inspection.readings.O_apparent_power.a": 0.7, "general_inspection.readings.O_apparent_power.b": 1.6, "general_inspection.readings.O_apparent_power.c": 1.8, "general_inspection.readings.P_output_power.a": 11.0, "general_inspection.readings.P_output_power.b": 19.0, "general_inspection.readings.P_output_power.c": 20.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.5, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.6, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 160.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 80.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 60.0, "comments_recommendation": "All annection cable with battery in secure procution.", "technician_name": "", "technician_id": 1110, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000446351.pdf | 4000446351 | {"station": "HAH", "date_time": "17/01/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 36.6, "general_inspection.readings.B_module_temperature.max": 49.4, "general_inspection.readings.C_battery_run_time": 332.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 271.0, "general_inspection.readings.F_battery_voltage_v.negative": 271.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 247.0, "general_inspection.readings.I_rectifier_voltage.b": 247.0, "general_inspection.readings.I_rectifier_voltage.c": 239.0, "general_inspection.readings.J_bypass_voltage.a": 248.0, "general_inspection.readings.J_bypass_voltage.b": 276.0, "general_inspection.readings.J_bypass_voltage.c": 239.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 1.11, "general_inspection.readings.L_output_current.b": 2.3, "general_inspection.readings.L_output_current.c": 2.7, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.5, "general_inspection.readings.M_active_power.c": 0.6, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.0, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 0.5, "general_inspection.readings.O_apparent_power.c": 0.6, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 8.0, "general_inspection.readings.P_output_power.c": 9.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.8, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 160.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 80.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 150.0, "comments_recommendation": "All equipment in good condition", "technician_name": "", "technician_id": "7222", "supervisor_name": "", "supervisor_id": "7111"}
SC_PM_QTR_UPS_4000576156.pdf | 4000576156 | {"station": "MAH", "date_time": "16/10/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 34.7, "general_inspection.readings.B_module_temperature.max": 41.6, "general_inspection.readings.C_battery_run_time": 122.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 243.0, "general_inspection.readings.I_rectifier_voltage.b": 242.0, "general_inspection.readings.I_rectifier_voltage.c": 243.0, "general_inspection.readings.J_bypass_voltage.a": 243.0, "general_inspection.readings.J_bypass_voltage.b": 243.0, "general_inspection.readings.J_bypass_voltage.c": 244.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 3.4, "general_inspection.readings.L_output_current.b": 6.2, "general_inspection.readings.L_output_current.c": 10.4, "general_inspection.readings.M_active_power.a": 0.7, "general_inspection.readings.M_active_power.b": 1.3, "general_inspection.readings.M_active_power.c": 2.2, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.3, "general_inspection.readings.N_reactive_power.c": 0.7, "general_inspection.readings.O_apparent_power.a": 0.8, "general_inspection.readings.O_apparent_power.b": 1.7, "general_inspection.readings.O_apparent_power.c": 2.5, "general_inspection.readings.P_output_power.a": 11.0, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 37.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All good condition", "technician_name": "", "technician_id": 19920, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000493791.pdf | 4000493791 | {"station": "MAH", "date_time": "16/10/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 34.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 136.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 271.0, "general_inspection.readings.F_battery_voltage_v.negative": 271.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.7, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 255.0, "general_inspection.readings.I_rectifier_voltage.b": 254.0, "general_inspection.readings.I_rectifier_voltage.c": 253.0, "general_inspection.readings.J_bypass_voltage.a": 255.0, "general_inspection.readings.J_bypass_voltage.b": 256.0, "general_inspection.readings.J_bypass_voltage.c": 256.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 3.2, "general_inspection.readings.L_output_current.b": 6.3, "general_inspection.readings.L_output_current.c": 7.6, "general_inspection.readings.M_active_power.a": 0.7, "general_inspection.readings.M_active_power.b": 1.5, "general_inspection.readings.M_active_power.c": 1.8, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.3, "general_inspection.readings.N_reactive_power.c": 0.5, "general_inspection.readings.O_apparent_power.a": 0.7, "general_inspection.readings.O_apparent_power.b": 1.5, "general_inspection.readings.O_apparent_power.c": 0.8, "general_inspection.readings.P_output_power.a": 11.0, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 27.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.5, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.7, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 160.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 80.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 60.0, "comments_recommendation": "", "technician_name": "", "technician_id": 7222, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000646818.pdf | 4000646818 | {"station": "MAH", "date_time": "16/10/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": null, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 36.0, "general_inspection.readings.B_module_temperature.max": 40.9, "general_inspection.readings.C_battery_run_time": 128.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 243.0, "general_inspection.readings.I_rectifier_voltage.b": 241.0, "general_inspection.readings.I_rectifier_voltage.c": 246.0, "general_inspection.readings.J_bypass_voltage.a": 243.0, "general_inspection.readings.J_bypass_voltage.b": 242.0, "general_inspection.readings.J_bypass_voltage.c": 245.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 3.6, "general_inspection.readings.L_output_current.b": 7.6, "general_inspection.readings.L_output_current.c": 9.6, "general_inspection.readings.M_active_power.a": 0.8, "general_inspection.readings.M_active_power.b": 1.6, "general_inspection.readings.M_active_power.c": 2.2, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.4, "general_inspection.readings.N_reactive_power.c": 0.6, "general_inspection.readings.O_apparent_power.a": 0.4, "general_inspection.readings.O_apparent_power.b": 1.6, "general_inspection.readings.O_apparent_power.c": 2.2, "general_inspection.readings.P_output_power.a": 12.0, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 34.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All equipment in good condition", "technician_name": "", "technician_id": 22547, "supervisor_name": "", "supervisor_id": 7202}
SC_PM_NA_UPS_NA_13.pdf |  | {"station": "MAH", "date_time": "16/07/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 35.2, "general_inspection.readings.B_module_temperature.max": 42.0, "general_inspection.readings.C_battery_run_time": 126.0, "general_inspection.readings.D_output_frequency": 50.04, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 248.0, "general_inspection.readings.I_rectifier_voltage.b": 247.0, "general_inspection.readings.I_rectifier_voltage.c": 249.0, "general_inspection.readings.J_bypass_voltage.a": 248.0, "general_inspection.readings.J_bypass_voltage.b": 248.0, "general_inspection.readings.J_bypass_voltage.c": 250.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 36.0, "general_inspection.readings.L_output_current.b": 6.0, "general_inspection.readings.L_output_current.c": 9.0, "general_inspection.readings.M_active_power.a": 0.8, "general_inspection.readings.M_active_power.b": 1.5, "general_inspection.readings.M_active_power.c": 2.0, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.3, "general_inspection.readings.N_reactive_power.c": 0.5, "general_inspection.readings.O_apparent_power.a": 0.4, "general_inspection.readings.O_apparent_power.b": 1.5, "general_inspection.readings.O_apparent_power.c": 2.2, "general_inspection.readings.P_output_power.a": 13.0, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 34.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All equipment in good condition", "technician_name": "", "technician_id": "9920", "supervisor_name": "", "supervisor_id": "7256"}
SC_PM_QTR_UPS_4000541165.pdf | 4000541165 | {"station": "MAH", "date_time": "16/07/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 65.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 100.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 80.0, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 207.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 245.0, "general_inspection.readings.I_rectifier_voltage.b": 245.0, "general_inspection.readings.I_rectifier_voltage.c": 247.0, "general_inspection.readings.J_bypass_voltage.a": 246.0, "general_inspection.readings.J_bypass_voltage.b": 246.0, "general_inspection.readings.J_bypass_voltage.c": 246.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 241.0, "general_inspection.readings.L_output_current.a": 5.2, "general_inspection.readings.L_output_current.b": 5.6, "general_inspection.readings.L_output_current.c": 10.4, "general_inspection.readings.M_active_power.a": 0.8, "general_inspection.readings.M_active_power.b": 1.4, "general_inspection.readings.M_active_power.c": 2.3, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.3, "general_inspection.readings.N_reactive_power.c": 0.6, "general_inspection.readings.O_apparent_power.a": 0.8, "general_inspection.readings.O_apparent_power.b": 1.4, "general_inspection.readings.O_apparent_power.c": 2.4, "general_inspection.readings.P_output_power.a": 12.0, "general_inspection.readings.P_output_power.b": 25.0, "general_inspection.readings.P_output_power.c": 38.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "one module operated", "technician_name": "", "technician_id": 7223, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000480697.pdf | 4000480697 | {"station": "MAH", "date_time": "16/07/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 30.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 129.6, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 271.0, "general_inspection.readings.F_battery_voltage_v.negative": 271.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.7, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 255.0, "general_inspection.readings.I_rectifier_voltage.b": 254.0, "general_inspection.readings.I_rectifier_voltage.c": 256.0, "general_inspection.readings.J_bypass_voltage.a": 255.0, "general_inspection.readings.J_bypass_voltage.b": 256.0, "general_inspection.readings.J_bypass_voltage.c": 256.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 237.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 3.2, "general_inspection.readings.L_output_current.b": 6.3, "general_inspection.readings.L_output_current.c": 7.6, "general_inspection.readings.M_active_power.a": 0.7, "general_inspection.readings.M_active_power.b": 15.0, "general_inspection.readings.M_active_power.c": 1.8, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.3, "general_inspection.readings.N_reactive_power.c": 0.5, "general_inspection.readings.O_apparent_power.a": 0.7, "general_inspection.readings.O_apparent_power.b": 1.5, "general_inspection.readings.O_apparent_power.c": 0.8, "general_inspection.readings.P_output_power.a": 11.0, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 27.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.8, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.6, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 160.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 80.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 60.0, "comments_recommendation": "OK", "technician_name": "ROHIZAN", "technician_id": 7223, "supervisor_name": "AZHAR YUNUS", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000608051.pdf | 4000608051 | {"station": "MAH", "date_time": "16/04/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 133.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.1, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 247.0, "general_inspection.readings.I_rectifier_voltage.b": 246.0, "general_inspection.readings.I_rectifier_voltage.c": 248.0, "general_inspection.readings.J_bypass_voltage.a": 248.0, "general_inspection.readings.J_bypass_voltage.b": 248.0, "general_inspection.readings.J_bypass_voltage.c": 249.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 2.7, "general_inspection.readings.L_output_current.b": 7.1, "general_inspection.readings.L_output_current.c": 9.6, "general_inspection.readings.M_active_power.a": 0.9, "general_inspection.readings.M_active_power.b": 1.5, "general_inspection.readings.M_active_power.c": 2.2, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.3, "general_inspection.readings.N_reactive_power.c": 0.6, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 1.5, "general_inspection.readings.O_apparent_power.c": 2.3, "general_inspection.readings.P_output_power.a": 9.0, "general_inspection.readings.P_output_power.b": 22.0, "general_inspection.readings.P_output_power.c": 35.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "Bank 1 TRANSFER to HanG TUAH. Module 1 Problem.Equipment in good condition", "technician_name": "", "technician_id": 20449, "supervisor_name": "", "supervisor_id": 7011}
SC_PM_QTR_UPS_4000530695.pdf | 4000530695 | {"station": "MAH", "date_time": "16/04/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 35.8, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 120.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 245.0, "general_inspection.readings.I_rectifier_voltage.b": 244.0, "general_inspection.readings.I_rectifier_voltage.c": 246.0, "general_inspection.readings.J_bypass_voltage.a": 245.0, "general_inspection.readings.J_bypass_voltage.b": 245.0, "general_inspection.readings.J_bypass_voltage.c": 245.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 2.7, "general_inspection.readings.L_output_current.b": 6.7, "general_inspection.readings.L_output_current.c": 9.6, "general_inspection.readings.M_active_power.a": 0.6, "general_inspection.readings.M_active_power.b": 1.5, "general_inspection.readings.M_active_power.c": 2.2, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.3, "general_inspection.readings.N_reactive_power.c": 0.5, "general_inspection.readings.O_apparent_power.a": 0.6, "general_inspection.readings.O_apparent_power.b": 1.6, "general_inspection.readings.O_apparent_power.c": 2.3, "general_inspection.readings.P_output_power.a": 10.0, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 37.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.3, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.2, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.5, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 120.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 60.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 60.0, "comments_recommendation": "", "technician_name": "", "technician_id": 7223, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000467093.pdf | 4000467093 | {"station": "MAH", "date_time": "16/04/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 32.2, "general_inspection.readings.B_module_temperature.max": 38.9, "general_inspection.readings.C_battery_run_time": 133.0, "general_inspection.readings.D_output_frequency": 50.01, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 271.0, "general_inspection.readings.F_battery_voltage_v.negative": 271.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 248.0, "general_inspection.readings.I_rectifier_voltage.b": 248.0, "general_inspection.readings.I_rectifier_voltage.c": 248.0, "general_inspection.readings.J_bypass_voltage.a": 248.0, "general_inspection.readings.J_bypass_voltage.b": 249.0, "general_inspection.readings.J_bypass_voltage.c": 249.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 2.0, "general_inspection.readings.L_output_current.b": null, "general_inspection.readings.L_output_current.c": 6.9, "general_inspection.readings.M_active_power.a": 0.4, "general_inspection.readings.M_active_power.b": 1.4, "general_inspection.readings.M_active_power.c": 2.4, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.8, "general_inspection.readings.O_apparent_power.a": 0.5, "general_inspection.readings.O_apparent_power.b": 1.4, "general_inspection.readings.O_apparent_power.c": 2.6, "general_inspection.readings.P_output_power.a": 7.0, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 37.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.6, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 180.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 60.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 60.0, "comments_recommendation": "all equipment in good conditions", "technician_name": "", "technician_id": "11727", "supervisor_name": "", "supervisor_id": "7111"}
SC_PM_QTR_UPS_4000467110.pdf | 4000467110 | {"station": "TUN", "date_time": "16/04/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 24.7, "general_inspection.readings.B_module_temperature.max": 22.6, "general_inspection.readings.C_battery_run_time": 122.0, "general_inspection.readings.D_output_frequency": 49.9, "general_inspection.readings.E_bypass_frequency": 49.6, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 768.3, "general_inspection.readings.G_battery_charge_car.negative": 268.1, "general_inspection.readings.H_discharge_current": 1.3, "general_inspection.readings.I_rectifier_voltage.a": null, "general_inspection.readings.I_rectifier_voltage.b": null, "general_inspection.readings.I_rectifier_voltage.c": null, "general_inspection.readings.J_bypass_voltage.a": 244.0, "general_inspection.readings.J_bypass_voltage.b": 243.0, "general_inspection.readings.J_bypass_voltage.c": 243.0, "general_inspection.readings.K_output_voltage.a": 241.0, "general_inspection.readings.K_output_voltage.b": 241.0, "general_inspection.readings.K_output_voltage.c": 241.0, "general_inspection.readings.L_output_current.a": 0.2, "general_inspection.readings.L_output_current.b": 2.1, "general_inspection.readings.L_output_current.c": 1.5, "general_inspection.readings.M_active_power.a": 0.4, "general_inspection.readings.M_active_power.b": 1.9, "general_inspection.readings.M_active_power.c": 2.4, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.5, "general_inspection.readings.O_apparent_power.a": 0.5, "general_inspection.readings.O_apparent_power.b": 1.4, "general_inspection.readings.O_apparent_power.c": 2.6, "general_inspection.readings.P_output_power.a": 7.0, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 36.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.4, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 110.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 60.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 105.0, "comments_recommendation": "all equipment in good conditions", "technician_name": "", "technician_id": "11727", "supervisor_name": "", "supervisor_id": "7111"}
SC_PM_QTR_UPS_4000668132.pdf | 4000668132 | {"station": "MAH", "date_time": "16/01/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": null, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 36.3, "general_inspection.readings.B_module_temperature.max": 42.8, "general_inspection.readings.C_battery_run_time": 125.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 244.0, "general_inspection.readings.I_rectifier_voltage.b": 243.0, "general_inspection.readings.I_rectifier_voltage.c": 246.0, "general_inspection.readings.J_bypass_voltage.a": 244.0, "general_inspection.readings.J_bypass_voltage.b": 244.0, "general_inspection.readings.J_bypass_voltage.c": 247.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 2.7, "general_inspection.readings.L_output_current.b": 6.7, "general_inspection.readings.L_output_current.c": 9.6, "general_inspection.readings.M_active_power.a": 0.8, "general_inspection.readings.M_active_power.b": 0.7, "general_inspection.readings.M_active_power.c": 2.3, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.5, "general_inspection.readings.N_reactive_power.c": 0.5, "general_inspection.readings.O_apparent_power.a": 0.8, "general_inspection.readings.O_apparent_power.b": 2.6, "general_inspection.readings.O_apparent_power.c": 2.2, "general_inspection.readings.P_output_power.a": 12.0, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 34.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "Bank A not available, All battery in good condition.", "technician_name": "", "technician_id": "22775", "supervisor_name": "", "supervisor_id": "7110"}
SC_PM_QTR_UPS_4000597813.pdf | 4000597813 | {"station": "MAH", "date_time": "16/01/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 39.0, "general_inspection.readings.B_module_temperature.max": 45.8, "general_inspection.readings.C_battery_run_time": 122.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 246.0, "general_inspection.readings.I_rectifier_voltage.b": 246.0, "general_inspection.readings.I_rectifier_voltage.c": 247.0, "general_inspection.readings.J_bypass_voltage.a": 247.0, "general_inspection.readings.J_bypass_voltage.b": 247.0, "general_inspection.readings.J_bypass_voltage.c": 248.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 3.3, "general_inspection.readings.L_output_current.b": 6.3, "general_inspection.readings.L_output_current.c": 9.5, "general_inspection.readings.M_active_power.a": 0.8, "general_inspection.readings.M_active_power.b": 1.6, "general_inspection.readings.M_active_power.c": 2.3, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.6, "general_inspection.readings.O_apparent_power.a": 0.8, "general_inspection.readings.O_apparent_power.b": 1.5, "general_inspection.readings.O_apparent_power.c": 2.3, "general_inspection.readings.P_output_power.a": 12.0, "general_inspection.readings.P_output_power.b": 22.0, "general_inspection.readings.P_output_power.c": 35.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": null, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": null, "battery_backup_test.turn_off_main_switch_breaker.status": null, "battery_backup_test.confirm_alarm_sounding.status": null, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": null, "battery_backup_test.switch_on_back_main_switch_breaker.status": null, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "1. Only used 1 module because module power failure (module 1)\n2. All batteries in good condition\n3. Equipment in good condition.", "technician_name": "", "technician_id": 20826, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000509102.pdf | 4000509102 | {"station": "MAH", "date_time": "16/01/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 30.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 136.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 271.0, "general_inspection.readings.F_battery_voltage_v.negative": 271.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.7, "general_inspection.readings.H_discharge_current": null, "general_inspection.readings.I_rectifier_voltage.a": 255.0, "general_inspection.readings.I_rectifier_voltage.b": 254.0, "general_inspection.readings.I_rectifier_voltage.c": 236.0, "general_inspection.readings.J_bypass_voltage.a": 255.0, "general_inspection.readings.J_bypass_voltage.b": 256.0, "general_inspection.readings.J_bypass_voltage.c": 256.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 2.2, "general_inspection.readings.L_output_current.b": 6.3, "general_inspection.readings.L_output_current.c": 7.6, "general_inspection.readings.M_active_power.a": 0.7, "general_inspection.readings.M_active_power.b": 1.5, "general_inspection.readings.M_active_power.c": 1.3, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.3, "general_inspection.readings.N_reactive_power.c": 0.5, "general_inspection.readings.O_apparent_power.a": 0.7, "general_inspection.readings.O_apparent_power.b": 1.5, "general_inspection.readings.O_apparent_power.c": 1.8, "general_inspection.readings.P_output_power.a": 11.0, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 27.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.2, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.4, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 160.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 80.0, "battery_backup_test.after.battery": 80.0, "battery_backup_test.battery_backup_time": 60.0, "comments_recommendation": "An eaupment modem and battery in good artition.", "technician_name": "", "technician_id": 7110, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000446338.pdf | 4000446338 | {"station": "MAH", "date_time": "16/01/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 34.1, "general_inspection.readings.B_module_temperature.max": 41.5, "general_inspection.readings.C_battery_run_time": 196.0, "general_inspection.readings.D_output_frequency": 80.0, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 271.0, "general_inspection.readings.F_battery_voltage_v.negative": 271.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 255.0, "general_inspection.readings.I_rectifier_voltage.b": 256.0, "general_inspection.readings.I_rectifier_voltage.c": 254.0, "general_inspection.readings.J_bypass_voltage.a": 255.0, "general_inspection.readings.J_bypass_voltage.b": 256.0, "general_inspection.readings.J_bypass_voltage.c": 254.0, "general_inspection.readings.K_output_voltage.a": 229.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 3.2, "general_inspection.readings.L_output_current.b": 6.1, "general_inspection.readings.L_output_current.c": 7.6, "general_inspection.readings.M_active_power.a": 0.7, "general_inspection.readings.M_active_power.b": 1.6, "general_inspection.readings.M_active_power.c": 1.8, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.3, "general_inspection.readings.N_reactive_power.c": 0.5, "general_inspection.readings.O_apparent_power.a": 0.7, "general_inspection.readings.O_apparent_power.b": 1.5, "general_inspection.readings.O_apparent_power.c": 1.8, "general_inspection.readings.P_output_power.a": 11.0, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 27.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.8, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.7, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 240.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 120.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 120.0, "comments_recommendation": "ok", "technician_name": "", "technician_id": 7222, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000647425.pdf | 4000647425 | {"station": "Tun", "date_time": "15/10/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 21.0, "general_inspection.readings.B_module_temperature.max": 23.0, "general_inspection.readings.C_battery_run_time": null, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 267.0, "general_inspection.readings.G_battery_charge_car.negative": 268.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 55.0, "general_inspection.readings.I_rectifier_voltage.b": 1.0, "general_inspection.readings.I_rectifier_voltage.c": 34.0, "general_inspection.readings.J_bypass_voltage.a": 242.0, "general_inspection.readings.J_bypass_voltage.b": 240.0, "general_inspection.readings.J_bypass_voltage.c": 243.0, "general_inspection.readings.K_output_voltage.a": 241.0, "general_inspection.readings.K_output_voltage.b": 241.0, "general_inspection.readings.K_output_voltage.c": 241.0, "general_inspection.readings.L_output_current.a": 0.2, "general_inspection.readings.L_output_current.b": 2.2, "general_inspection.readings.L_output_current.c": 1.8, "general_inspection.readings.M_active_power.a": 0.1, "general_inspection.readings.M_active_power.b": 0.4, "general_inspection.readings.M_active_power.c": 0.3, "general_inspection.readings.N_reactive_power.a": 0.4, "general_inspection.readings.N_reactive_power.b": 2.0, "general_inspection.readings.N_reactive_power.c": 1.6, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.0, "general_inspection.readings.O_apparent_power.c": 1.0, "general_inspection.readings.P_output_power.a": 84.4, "general_inspection.readings.P_output_power.b": 16.3, "general_inspection.readings.P_output_power.c": 15.9, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All in good condition", "technician_name": "", "technician_id": 19922, "supervisor_name": "", "supervisor_id": 7248}
SC_PM_QTR_UPS_4000576195.pdf | 4000576195 | {"station": "Tun", "date_time": "15/10/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": null, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 261.0, "general_inspection.readings.F_battery_voltage_v.negative": 261.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": null, "general_inspection.readings.I_rectifier_voltage.a": null, "general_inspection.readings.I_rectifier_voltage.b": null, "general_inspection.readings.I_rectifier_voltage.c": null, "general_inspection.readings.J_bypass_voltage.a": 243.0, "general_inspection.readings.J_bypass_voltage.b": 242.0, "general_inspection.readings.J_bypass_voltage.c": 244.0, "general_inspection.readings.K_output_voltage.a": 241.0, "general_inspection.readings.K_output_voltage.b": 241.0, "general_inspection.readings.K_output_voltage.c": 241.0, "general_inspection.readings.L_output_current.a": 1.0, "general_inspection.readings.L_output_current.b": 8.1, "general_inspection.readings.L_output_current.c": 6.5, "general_inspection.readings.M_active_power.a": 0.2, "general_inspection.readings.M_active_power.b": 1.6, "general_inspection.readings.M_active_power.c": 1.1, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 2.0, "general_inspection.readings.N_reactive_power.c": 1.6, "general_inspection.readings.O_apparent_power.a": 0.0, "general_inspection.readings.O_apparent_power.b": 0.8, "general_inspection.readings.O_apparent_power.c": 1.0, "general_inspection.readings.P_output_power.a": 0.8, "general_inspection.readings.P_output_power.b": 0.84, "general_inspection.readings.P_output_power.c": 0.75, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.2, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.5, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 186.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 68.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 60.0, "comments_recommendation": "good condition", "technician_name": "", "technician_id": 7248, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000509049.pdf | 4000509049 | {"station": "TUN", "date_time": "15/10/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 33.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 180.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 241.0, "general_inspection.readings.F_battery_voltage_v.negative": 242.0, "general_inspection.readings.G_battery_charge_car.positive": 0.2, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 1.9, "general_inspection.readings.I_rectifier_voltage.a": 243.0, "general_inspection.readings.I_rectifier_voltage.b": 244.0, "general_inspection.readings.I_rectifier_voltage.c": 245.0, "general_inspection.readings.J_bypass_voltage.a": 244.0, "general_inspection.readings.J_bypass_voltage.b": 243.0, "general_inspection.readings.J_bypass_voltage.c": 244.0, "general_inspection.readings.K_output_voltage.a": 241.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 244.0, "general_inspection.readings.L_output_current.a": 1.9, "general_inspection.readings.L_output_current.b": 6.5, "general_inspection.readings.L_output_current.c": 6.4, "general_inspection.readings.M_active_power.a": 0.2, "general_inspection.readings.M_active_power.b": 0.1, "general_inspection.readings.M_active_power.c": 0.1, "general_inspection.readings.N_reactive_power.a": 0.3, "general_inspection.readings.N_reactive_power.b": 1.6, "general_inspection.readings.N_reactive_power.c": 1.7, "general_inspection.readings.O_apparent_power.a": 0.1, "general_inspection.readings.O_apparent_power.b": 1.1, "general_inspection.readings.O_apparent_power.c": 1.1, "general_inspection.readings.P_output_power.a": 3.5, "general_inspection.readings.P_output_power.b": 3.2, "general_inspection.readings.P_output_power.c": 3.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.3, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.5, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.7, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 180.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 90.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 90.0, "comments_recommendation": "", "technician_name": "", "technician_id": "7222", "supervisor_name": "", "supervisor_id": "7111"}
SC_PM_NA_UPS_NA_4.pdf |  | {"station": "TUN", "date_time": "15/07/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 21.5, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": null, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 267.7, "general_inspection.readings.F_battery_voltage_v.negative": 267.7, "general_inspection.readings.G_battery_charge_car.positive": 268.2, "general_inspection.readings.G_battery_charge_car.negative": null, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 55.0, "general_inspection.readings.I_rectifier_voltage.b": 1.0, "general_inspection.readings.I_rectifier_voltage.c": 34.0, "general_inspection.readings.J_bypass_voltage.a": 245.3, "general_inspection.readings.J_bypass_voltage.b": 243.5, "general_inspection.readings.J_bypass_voltage.c": 246.8, "general_inspection.readings.K_output_voltage.a": 241.5, "general_inspection.readings.K_output_voltage.b": 241.3, "general_inspection.readings.K_output_voltage.c": 241.3, "general_inspection.readings.L_output_current.a": 1.8, "general_inspection.readings.L_output_current.b": 8.0, "general_inspection.readings.L_output_current.c": 6.9, "general_inspection.readings.M_active_power.a": 0.2, "general_inspection.readings.M_active_power.b": 1.7, "general_inspection.readings.M_active_power.c": 1.2, "general_inspection.readings.N_reactive_power.a": 0.4, "general_inspection.readings.N_reactive_power.b": 2.0, "general_inspection.readings.N_reactive_power.c": 1.6, "general_inspection.readings.O_apparent_power.a": 0.7, "general_inspection.readings.O_apparent_power.b": 1.0, "general_inspection.readings.O_apparent_power.c": 1.0, "general_inspection.readings.P_output_power.a": 84.4, "general_inspection.readings.P_output_power.b": 16.3, "general_inspection.readings.P_output_power.c": 15.9, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All in good condition", "technician_name": "", "technician_id": "20450", "supervisor_name": "", "supervisor_id": 7262}
SC_PM_QTR_UPS_4000541175.pdf | 4000541175 | {"station": "TUN", "date_time": "15/07/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": null, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 247.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": null, "general_inspection.readings.I_rectifier_voltage.a": null, "general_inspection.readings.I_rectifier_voltage.b": null, "general_inspection.readings.I_rectifier_voltage.c": null, "general_inspection.readings.J_bypass_voltage.a": 243.0, "general_inspection.readings.J_bypass_voltage.b": 242.0, "general_inspection.readings.J_bypass_voltage.c": 244.0, "general_inspection.readings.K_output_voltage.a": 241.0, "general_inspection.readings.K_output_voltage.b": 241.0, "general_inspection.readings.K_output_voltage.c": 241.0, "general_inspection.readings.L_output_current.a": 1.6, "general_inspection.readings.L_output_current.b": 8.1, "general_inspection.readings.L_output_current.c": 6.5, "general_inspection.readings.M_active_power.a": 0.2, "general_inspection.readings.M_active_power.b": 1.6, "general_inspection.readings.M_active_power.c": 1.1, "general_inspection.readings.N_reactive_power.a": 0.4, "general_inspection.readings.N_reactive_power.b": 2.0, "general_inspection.readings.N_reactive_power.c": 1.6, "general_inspection.readings.O_apparent_power.a": 0.0, "general_inspection.readings.O_apparent_power.b": 0.8, "general_inspection.readings.O_apparent_power.c": 1.6, "general_inspection.readings.P_output_power.a": 0.8, "general_inspection.readings.P_output_power.b": 0.84, "general_inspection.readings.P_output_power.c": 0.75, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "good condition.", "technician_name": "", "technician_id": 7223, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000480722.pdf | 4000480722 | {"station": "TUN", "date_time": "15/07/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 33.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 180.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 241.0, "general_inspection.readings.F_battery_voltage_v.negative": 242.0, "general_inspection.readings.G_battery_charge_car.positive": 0.2, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 1.9, "general_inspection.readings.I_rectifier_voltage.a": 243.0, "general_inspection.readings.I_rectifier_voltage.b": 244.0, "general_inspection.readings.I_rectifier_voltage.c": 245.0, "general_inspection.readings.J_bypass_voltage.a": 244.0, "general_inspection.readings.J_bypass_voltage.b": 243.0, "general_inspection.readings.J_bypass_voltage.c": 244.0, "general_inspection.readings.K_output_voltage.a": 241.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 244.0, "general_inspection.readings.L_output_current.a": 1.9, "general_inspection.readings.L_output_current.b": 6.5, "general_inspection.readings.L_output_current.c": 6.4, "general_inspection.readings.M_active_power.a": 0.2, "general_inspection.readings.M_active_power.b": 0.1, "general_inspection.readings.M_active_power.c": 1.1, "general_inspection.readings.N_reactive_power.a": 0.3, "general_inspection.readings.N_reactive_power.b": 1.6, "general_inspection.readings.N_reactive_power.c": 1.7, "general_inspection.readings.O_apparent_power.a": 0.1, "general_inspection.readings.O_apparent_power.b": 1.1, "general_inspection.readings.O_apparent_power.c": 1.1, "general_inspection.readings.P_output_power.a": 3.5, "general_inspection.readings.P_output_power.b": 3.2, "general_inspection.readings.P_output_power.c": 3.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.3, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.5, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.0, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 180.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 90.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 90.0, "comments_recommendation": "ok", "technician_name": "ROHIZAN", "technician_id": 7223, "supervisor_name": "AZHAR YUNUS", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000608083.pdf | 4000608083 | {"station": "TUN", "date_time": "15/04/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 30.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 70.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 55.0, "general_inspection.readings.I_rectifier_voltage.b": 1.0, "general_inspection.readings.I_rectifier_voltage.c": 34.0, "general_inspection.readings.J_bypass_voltage.a": 244.0, "general_inspection.readings.J_bypass_voltage.b": 244.0, "general_inspection.readings.J_bypass_voltage.c": 246.0, "general_inspection.readings.K_output_voltage.a": 241.0, "general_inspection.readings.K_output_voltage.b": 241.0, "general_inspection.readings.K_output_voltage.c": 241.0, "general_inspection.readings.L_output_current.a": 1.9, "general_inspection.readings.L_output_current.b": 8.3, "general_inspection.readings.L_output_current.c": 6.5, "general_inspection.readings.M_active_power.a": 0.2, "general_inspection.readings.M_active_power.b": 1.7, "general_inspection.readings.M_active_power.c": 1.2, "general_inspection.readings.N_reactive_power.a": 0.4, "general_inspection.readings.N_reactive_power.b": 2.0, "general_inspection.readings.N_reactive_power.c": 1.6, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.0, "general_inspection.readings.O_apparent_power.c": 1.0, "general_inspection.readings.P_output_power.a": 8.4, "general_inspection.readings.P_output_power.b": 16.3, "general_inspection.readings.P_output_power.c": 15.9, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "all equipment are in good condition", "technician_name": "", "technician_id": 20449, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000520523.pdf | 4000520523 | {"station": "TUN", "date_time": "15/04/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 54.0, "general_inspection.readings.D_output_frequency": 49.9, "general_inspection.readings.E_bypass_frequency": 49.5, "general_inspection.readings.F_battery_voltage_v.positive": 249.0, "general_inspection.readings.F_battery_voltage_v.negative": 269.0, "general_inspection.readings.G_battery_charge_car.positive": null, "general_inspection.readings.G_battery_charge_car.negative": null, "general_inspection.readings.H_discharge_current": null, "general_inspection.readings.I_rectifier_voltage.a": null, "general_inspection.readings.I_rectifier_voltage.b": null, "general_inspection.readings.I_rectifier_voltage.c": null, "general_inspection.readings.J_bypass_voltage.a": 240.0, "general_inspection.readings.J_bypass_voltage.b": 239.0, "general_inspection.readings.J_bypass_voltage.c": 241.0, "general_inspection.readings.K_output_voltage.a": 241.0, "general_inspection.readings.K_output_voltage.b": 241.0, "general_inspection.readings.K_output_voltage.c": 247.0, "general_inspection.readings.L_output_current.a": 1.9, "general_inspection.readings.L_output_current.b": 8.2, "general_inspection.readings.L_output_current.c": 6.4, "general_inspection.readings.M_active_power.a": 0.1, "general_inspection.readings.M_active_power.b": 0.5, "general_inspection.readings.M_active_power.c": 0.5, "general_inspection.readings.N_reactive_power.a": null, "general_inspection.readings.N_reactive_power.b": null, "general_inspection.readings.N_reactive_power.c": null, "general_inspection.readings.O_apparent_power.a": 0.5, "general_inspection.readings.O_apparent_power.b": 0.5, "general_inspection.readings.O_apparent_power.c": 0.4, "general_inspection.readings.P_output_power.a": null, "general_inspection.readings.P_output_power.b": null, "general_inspection.readings.P_output_power.c": null, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.3, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.4, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 300.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 180.0, "battery_backup_test.after.battery": 60.0, "battery_backup_test.battery_backup_time": 10.0, "comments_recommendation": "", "technician_name": "", "technician_id": 7223, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000668027.pdf | 4000668027 | {"station": "TUN", "date_time": "15/01/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 30.2, "general_inspection.readings.B_module_temperature.max": 31.3, "general_inspection.readings.C_battery_run_time": 230.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 244.0, "general_inspection.readings.I_rectifier_voltage.b": 243.0, "general_inspection.readings.I_rectifier_voltage.c": 246.0, "general_inspection.readings.J_bypass_voltage.a": 244.0, "general_inspection.readings.J_bypass_voltage.b": 244.0, "general_inspection.readings.J_bypass_voltage.c": 247.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 2.7, "general_inspection.readings.L_output_current.b": 6.2, "general_inspection.readings.L_output_current.c": 9.6, "general_inspection.readings.M_active_power.a": 0.8, "general_inspection.readings.M_active_power.b": 0.7, "general_inspection.readings.M_active_power.c": 2.3, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.7, "general_inspection.readings.N_reactive_power.c": 2.3, "general_inspection.readings.O_apparent_power.a": 0.8, "general_inspection.readings.O_apparent_power.b": 2.6, "general_inspection.readings.O_apparent_power.c": 2.2, "general_inspection.readings.P_output_power.a": 12.0, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 34.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "all equiptment in good conditions", "technician_name": "", "technician_id": 11727, "supervisor_name": "", "supervisor_id": 11727}
SC_PM_QTR_UPS_4000597877.pdf | 4000597877 | {"station": "TUN", "date_time": "15/01/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 30.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 70.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 267.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 55.0, "general_inspection.readings.I_rectifier_voltage.b": 1.0, "general_inspection.readings.I_rectifier_voltage.c": 34.0, "general_inspection.readings.J_bypass_voltage.a": 244.0, "general_inspection.readings.J_bypass_voltage.b": 244.0, "general_inspection.readings.J_bypass_voltage.c": 246.0, "general_inspection.readings.K_output_voltage.a": 241.0, "general_inspection.readings.K_output_voltage.b": 241.0, "general_inspection.readings.K_output_voltage.c": 241.0, "general_inspection.readings.L_output_current.a": 1.9, "general_inspection.readings.L_output_current.b": 8.3, "general_inspection.readings.L_output_current.c": 6.5, "general_inspection.readings.M_active_power.a": 0.2, "general_inspection.readings.M_active_power.b": 1.7, "general_inspection.readings.M_active_power.c": 1.2, "general_inspection.readings.N_reactive_power.a": 0.4, "general_inspection.readings.N_reactive_power.b": 2.0, "general_inspection.readings.N_reactive_power.c": 1.6, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.0, "general_inspection.readings.O_apparent_power.c": 1.0, "general_inspection.readings.P_output_power.a": 84.4, "general_inspection.readings.P_output_power.b": 16.3, "general_inspection.readings.P_output_power.c": 15.9, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All equipment is in good condition", "technician_name": "", "technician_id": 19898, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000509048.pdf | 4000509048 | {"station": "TUN", "date_time": "15/01/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 24.0, "general_inspection.readings.B_module_temperature.max": 26.0, "general_inspection.readings.C_battery_run_time": 360.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 267.6, "general_inspection.readings.F_battery_voltage_v.negative": 267.8, "general_inspection.readings.G_battery_charge_car.positive": 241.2, "general_inspection.readings.G_battery_charge_car.negative": 241.3, "general_inspection.readings.H_discharge_current": null, "general_inspection.readings.I_rectifier_voltage.a": 240.0, "general_inspection.readings.I_rectifier_voltage.b": 239.0, "general_inspection.readings.I_rectifier_voltage.c": 241.0, "general_inspection.readings.J_bypass_voltage.a": 240.0, "general_inspection.readings.J_bypass_voltage.b": 239.0, "general_inspection.readings.J_bypass_voltage.c": 241.0, "general_inspection.readings.K_output_voltage.a": 241.0, "general_inspection.readings.K_output_voltage.b": 241.0, "general_inspection.readings.K_output_voltage.c": 241.0, "general_inspection.readings.L_output_current.a": 1.9, "general_inspection.readings.L_output_current.b": 7.9, "general_inspection.readings.L_output_current.c": 6.9, "general_inspection.readings.M_active_power.a": 0.2, "general_inspection.readings.M_active_power.b": 1.7, "general_inspection.readings.M_active_power.c": 1.1, "general_inspection.readings.N_reactive_power.a": 0.2, "general_inspection.readings.N_reactive_power.b": 1.9, "general_inspection.readings.N_reactive_power.c": 1.4, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.0, "general_inspection.readings.O_apparent_power.c": 1.0, "general_inspection.readings.P_output_power.a": 3.4, "general_inspection.readings.P_output_power.b": 14.3, "general_inspection.readings.P_output_power.c": 11.2, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.2, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.5, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 186.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 68.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 68.0, "comments_recommendation": "All equipment module and battery in good condition.", "technician_name": "", "technician_id": 7110, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_QTR_UPS_4000446286.pdf | 4000446286 | {"station": "TUN", "date_time": "15/01/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 34.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 180.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 241.0, "general_inspection.readings.F_battery_voltage_v.negative": 242.0, "general_inspection.readings.G_battery_charge_car.positive": 0.2, "general_inspection.readings.G_battery_charge_car.negative": 0.1, "general_inspection.readings.H_discharge_current": 1.9, "general_inspection.readings.I_rectifier_voltage.a": 243.0, "general_inspection.readings.I_rectifier_voltage.b": 241.0, "general_inspection.readings.I_rectifier_voltage.c": 245.0, "general_inspection.readings.J_bypass_voltage.a": 243.0, "general_inspection.readings.J_bypass_voltage.b": 244.0, "general_inspection.readings.J_bypass_voltage.c": 244.0, "general_inspection.readings.K_output_voltage.a": 241.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 244.0, "general_inspection.readings.L_output_current.a": 1.9, "general_inspection.readings.L_output_current.b": 6.5, "general_inspection.readings.L_output_current.c": 4.0, "general_inspection.readings.M_active_power.a": 0.2, "general_inspection.readings.M_active_power.b": 0.1, "general_inspection.readings.M_active_power.c": 1.1, "general_inspection.readings.N_reactive_power.a": 0.3, "general_inspection.readings.N_reactive_power.b": 1.6, "general_inspection.readings.N_reactive_power.c": 1.7, "general_inspection.readings.O_apparent_power.a": 0.1, "general_inspection.readings.O_apparent_power.b": 1.1, "general_inspection.readings.O_apparent_power.c": 1.1, "general_inspection.readings.P_output_power.a": 3.5, "general_inspection.readings.P_output_power.b": 3.2, "general_inspection.readings.P_output_power.c": 3.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.2, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.5, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.4, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 180.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 90.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 90.0, "comments_recommendation": "ok", "technician_name": "", "technician_id": 7110, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_NA_UPS_NA_1 (7).pdf |  | {"station": "KLS", "date_time": "14/10/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 35.2, "general_inspection.readings.B_module_temperature.max": 43.6, "general_inspection.readings.C_battery_run_time": 224.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 256.0, "general_inspection.readings.I_rectifier_voltage.b": 255.0, "general_inspection.readings.I_rectifier_voltage.c": 257.0, "general_inspection.readings.J_bypass_voltage.a": 255.0, "general_inspection.readings.J_bypass_voltage.b": 255.0, "general_inspection.readings.J_bypass_voltage.c": 256.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 238.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 2.3, "general_inspection.readings.L_output_current.b": 3.8, "general_inspection.readings.L_output_current.c": 5.3, "general_inspection.readings.M_active_power.a": 0.5, "general_inspection.readings.M_active_power.b": 0.9, "general_inspection.readings.M_active_power.c": 1.2, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.0, "general_inspection.readings.O_apparent_power.a": 0.5, "general_inspection.readings.O_apparent_power.b": 0.9, "general_inspection.readings.O_apparent_power.c": 1.2, "general_inspection.readings.P_output_power.a": 8.0, "general_inspection.readings.P_output_power.b": 13.0, "general_inspection.readings.P_output_power.c": 19.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "-Bank A, B, C temporary take out by Adc", "technician_name": "", "technician_id": 19922, "supervisor_name": "", "supervisor_id": 7248}
SC_PM_NA_UPS_NA_1 (1).pdf |  | {"station": "KLS", "date_time": "14/10/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 34.8, "general_inspection.readings.B_module_temperature.max": 41.6, "general_inspection.readings.C_battery_run_time": 210.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 255.0, "general_inspection.readings.I_rectifier_voltage.b": 254.0, "general_inspection.readings.I_rectifier_voltage.c": 256.0, "general_inspection.readings.J_bypass_voltage.a": 254.0, "general_inspection.readings.J_bypass_voltage.b": 254.0, "general_inspection.readings.J_bypass_voltage.c": 255.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 2.5, "general_inspection.readings.L_output_current.b": 5.9, "general_inspection.readings.L_output_current.c": 6.3, "general_inspection.readings.M_active_power.a": 0.6, "general_inspection.readings.M_active_power.b": 0.8, "general_inspection.readings.M_active_power.c": 1.4, "general_inspection.readings.N_reactive_power.a": 10.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.2, "general_inspection.readings.O_apparent_power.a": 0.5, "general_inspection.readings.O_apparent_power.b": 0.9, "general_inspection.readings.O_apparent_power.c": 1.5, "general_inspection.readings.P_output_power.a": 8.0, "general_inspection.readings.P_output_power.b": 13.0, "general_inspection.readings.P_output_power.c": 22.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.7, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.6, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 100.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 60.0, "battery_backup_test.after.battery": 80.0, "battery_backup_test.battery_backup_time": 120.0, "comments_recommendation": "connection connector cable secure and system in good condition.", "technician_name": "", "technician_id": 7110, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_NA_UPS_NA (9).pdf |  | {"station": "KLS", "date_time": "2025-01-14T00:00:00", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 214.0, "general_inspection.readings.D_output_frequency": 50.05, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 255.0, "general_inspection.readings.I_rectifier_voltage.b": 253.0, "general_inspection.readings.I_rectifier_voltage.c": 256.0, "general_inspection.readings.J_bypass_voltage.a": 254.0, "general_inspection.readings.J_bypass_voltage.b": 256.0, "general_inspection.readings.J_bypass_voltage.c": 255.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 238.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 2.3, "general_inspection.readings.L_output_current.b": 4.7, "general_inspection.readings.L_output_current.c": 5.8, "general_inspection.readings.M_active_power.a": 0.5, "general_inspection.readings.M_active_power.b": 0.9, "general_inspection.readings.M_active_power.c": 1.3, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.0, "general_inspection.readings.O_apparent_power.a": 0.5, "general_inspection.readings.O_apparent_power.b": 1.0, "general_inspection.readings.O_apparent_power.c": 1.3, "general_inspection.readings.P_output_power.a": 8.0, "general_inspection.readings.P_output_power.b": 16.0, "general_inspection.readings.P_output_power.c": 20.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "The UPS only use one bank and one breaker. Everything is in good condition. This up's also use two module.", "technician_name": "", "technician_id": 22778, "supervisor_name": "", "supervisor_id": 7110}
SC_PM_NA_UPS_NA_10.pdf |  | {"station": "KLS", "date_time": "14/07/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 32.1, "general_inspection.readings.B_module_temperature.max": 40.3, "general_inspection.readings.C_battery_run_time": 212.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 269.0, "general_inspection.readings.F_battery_voltage_v.negative": 270.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 257.0, "general_inspection.readings.I_rectifier_voltage.b": 255.0, "general_inspection.readings.I_rectifier_voltage.c": 258.0, "general_inspection.readings.J_bypass_voltage.a": null, "general_inspection.readings.J_bypass_voltage.b": null, "general_inspection.readings.J_bypass_voltage.c": null, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 238.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 2.3, "general_inspection.readings.L_output_current.b": 4.2, "general_inspection.readings.L_output_current.c": 5.7, "general_inspection.readings.M_active_power.a": 0.5, "general_inspection.readings.M_active_power.b": 0.8, "general_inspection.readings.M_active_power.c": 1.3, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.5, "general_inspection.readings.O_apparent_power.b": 0.8, "general_inspection.readings.O_apparent_power.c": 1.2, "general_inspection.readings.P_output_power.a": 8.0, "general_inspection.readings.P_output_power.b": 14.0, "general_inspection.readings.P_output_power.c": 19.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All in good condition", "technician_name": "", "technician_id": 20450, "supervisor_name": "", "supervisor_id": 7262}
SC_PM_NA_UPS_NA (1).pdf |  | {"station": "KLS", "date_time": "14/07/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 40.1, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 49.0, "general_inspection.readings.D_output_frequency": 14.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 20.7, "general_inspection.readings.F_battery_voltage_v.negative": 24.8, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 248.0, "general_inspection.readings.I_rectifier_voltage.b": 248.0, "general_inspection.readings.I_rectifier_voltage.c": 247.0, "general_inspection.readings.J_bypass_voltage.a": 249.0, "general_inspection.readings.J_bypass_voltage.b": 248.0, "general_inspection.readings.J_bypass_voltage.c": 248.0, "general_inspection.readings.K_output_voltage.a": 230.0, "general_inspection.readings.K_output_voltage.b": 230.0, "general_inspection.readings.K_output_voltage.c": 231.0, "general_inspection.readings.L_output_current.a": 5.3, "general_inspection.readings.L_output_current.b": 5.3, "general_inspection.readings.L_output_current.c": 10.3, "general_inspection.readings.M_active_power.a": 1.2, "general_inspection.readings.M_active_power.b": 1.2, "general_inspection.readings.M_active_power.c": 2.3, "general_inspection.readings.N_reactive_power.a": 0.3, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.4, "general_inspection.readings.O_apparent_power.a": 1.2, "general_inspection.readings.O_apparent_power.b": 1.2, "general_inspection.readings.O_apparent_power.c": 2.3, "general_inspection.readings.P_output_power.a": 19.0, "general_inspection.readings.P_output_power.b": 10.0, "general_inspection.readings.P_output_power.c": 25.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.7, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.05, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 100.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 60.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 120.0, "comments_recommendation": "", "technician_name": "", "technician_id": 7222, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_NA_UPS_NA (5).pdf |  | {"station": "KLS", "date_time": "14/04/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 34.1, "general_inspection.readings.B_module_temperature.max": 40.9, "general_inspection.readings.C_battery_run_time": 104.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 268.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 256.0, "general_inspection.readings.I_rectifier_voltage.b": 254.0, "general_inspection.readings.I_rectifier_voltage.c": 257.0, "general_inspection.readings.J_bypass_voltage.a": 255.0, "general_inspection.readings.J_bypass_voltage.b": 254.0, "general_inspection.readings.J_bypass_voltage.c": 257.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 5.0, "general_inspection.readings.L_output_current.b": 8.1, "general_inspection.readings.L_output_current.c": 12.1, "general_inspection.readings.M_active_power.a": 1.1, "general_inspection.readings.M_active_power.b": 1.9, "general_inspection.readings.M_active_power.c": 2.6, "general_inspection.readings.N_reactive_power.a": 0.3, "general_inspection.readings.N_reactive_power.b": 0.6, "general_inspection.readings.N_reactive_power.c": 0.5, "general_inspection.readings.O_apparent_power.a": 1.1, "general_inspection.readings.O_apparent_power.b": 1.9, "general_inspection.readings.O_apparent_power.c": 2.7, "general_inspection.readings.P_output_power.a": 17.0, "general_inspection.readings.P_output_power.b": 29.0, "general_inspection.readings.P_output_power.c": 41.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All equipment in good Condition", "technician_name": "", "technician_id": 20449, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_NA_UPS_NA_1 (2).pdf |  | {"station": "KLS", "date_time": "14/04/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 36.7, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 107.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 268.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 253.0, "general_inspection.readings.I_rectifier_voltage.b": 253.0, "general_inspection.readings.I_rectifier_voltage.c": 254.0, "general_inspection.readings.J_bypass_voltage.a": 253.0, "general_inspection.readings.J_bypass_voltage.b": 253.0, "general_inspection.readings.J_bypass_voltage.c": 254.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 5.0, "general_inspection.readings.L_output_current.b": 7.9, "general_inspection.readings.L_output_current.c": 11.3, "general_inspection.readings.M_active_power.a": 1.1, "general_inspection.readings.M_active_power.b": 1.5, "general_inspection.readings.M_active_power.c": 2.8, "general_inspection.readings.N_reactive_power.a": 0.3, "general_inspection.readings.N_reactive_power.b": 0.5, "general_inspection.readings.N_reactive_power.c": 10.5, "general_inspection.readings.O_apparent_power.a": 1.2, "general_inspection.readings.O_apparent_power.b": 1.8, "general_inspection.readings.O_apparent_power.c": 2.8, "general_inspection.readings.P_output_power.a": 17.0, "general_inspection.readings.P_output_power.b": 22.0, "general_inspection.readings.P_output_power.c": 42.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.3, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.1, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.2, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 102.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 60.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 40.0, "comments_recommendation": "1 Module Foil/problem", "technician_name": "", "technician_id": 7223, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_NA_UPS_NA.pdf |  | {"station": "KLS", "date_time": "14/04/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": null, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 32.2, "general_inspection.readings.B_module_temperature.max": 38.9, "general_inspection.readings.C_battery_run_time": 150.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 271.0, "general_inspection.readings.F_battery_voltage_v.negative": 271.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 248.0, "general_inspection.readings.I_rectifier_voltage.b": 248.0, "general_inspection.readings.I_rectifier_voltage.c": 248.0, "general_inspection.readings.J_bypass_voltage.a": null, "general_inspection.readings.J_bypass_voltage.b": null, "general_inspection.readings.J_bypass_voltage.c": null, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 20.0, "general_inspection.readings.L_output_current.b": 6.9, "general_inspection.readings.L_output_current.c": 10.3, "general_inspection.readings.M_active_power.a": 0.4, "general_inspection.readings.M_active_power.b": 1.4, "general_inspection.readings.M_active_power.c": 2.4, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.5, "general_inspection.readings.O_apparent_power.a": 0.5, "general_inspection.readings.O_apparent_power.b": 1.4, "general_inspection.readings.O_apparent_power.c": 2.0, "general_inspection.readings.P_output_power.a": 7.0, "general_inspection.readings.P_output_power.b": 23.0, "general_inspection.readings.P_output_power.c": 36.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 13.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 13.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 13.4, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": null, "battery_backup_test.switch_on_back_main_switch_breaker.status": null, "battery_backup_test.before.time_minutes": 150.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 80.0, "battery_backup_test.after.battery": 80.0, "battery_backup_test.battery_backup_time": 50.0, "comments_recommendation": "all equitment in good conditions", "technician_name": "", "technician_id": "11727", "supervisor_name": "", "supervisor_id": "7111"}
SC_PM_NA_UPS_NA (8).pdf |  | {"station": "KLS", "date_time": "14/01/2025", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": null, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 214.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 267.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 255.0, "general_inspection.readings.I_rectifier_voltage.b": 253.0, "general_inspection.readings.I_rectifier_voltage.c": 256.0, "general_inspection.readings.J_bypass_voltage.a": 254.0, "general_inspection.readings.J_bypass_voltage.b": 256.0, "general_inspection.readings.J_bypass_voltage.c": 255.0, "general_inspection.readings.K_output_voltage.a": 239.0, "general_inspection.readings.K_output_voltage.b": 238.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 2.3, "general_inspection.readings.L_output_current.b": 4.7, "general_inspection.readings.L_output_current.c": 5.8, "general_inspection.readings.M_active_power.a": 0.5, "general_inspection.readings.M_active_power.b": 0.9, "general_inspection.readings.M_active_power.c": 1.3, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.0, "general_inspection.readings.O_apparent_power.a": 0.5, "general_inspection.readings.O_apparent_power.b": 1.0, "general_inspection.readings.O_apparent_power.c": 1.3, "general_inspection.readings.P_output_power.a": 8.0, "general_inspection.readings.P_output_power.b": 16.0, "general_inspection.readings.P_output_power.c": 20.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": null, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": null, "servicing_and_cleaning.check_everything__normal.status": null, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "The UPS only use one bank and one breaker. Everything is in good condition. This ups also use two module.", "technician_name": "", "technician_id": 22778, "supervisor_name": "", "supervisor_id": 7110}
SC_PM_NA_UPS_NA (4).pdf |  | {"station": "KLS", "date_time": "14/01/2024", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 34.2, "general_inspection.readings.B_module_temperature.max": 40.9, "general_inspection.readings.C_battery_run_time": 101.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 268.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 256.0, "general_inspection.readings.I_rectifier_voltage.b": 256.0, "general_inspection.readings.I_rectifier_voltage.c": 258.0, "general_inspection.readings.J_bypass_voltage.a": 256.0, "general_inspection.readings.J_bypass_voltage.b": 256.0, "general_inspection.readings.J_bypass_voltage.c": 257.0, "general_inspection.readings.K_output_voltage.a": null, "general_inspection.readings.K_output_voltage.b": null, "general_inspection.readings.K_output_voltage.c": null, "general_inspection.readings.L_output_current.a": 4.9, "general_inspection.readings.L_output_current.b": 7.6, "general_inspection.readings.L_output_current.c": 11.8, "general_inspection.readings.M_active_power.a": 1.1, "general_inspection.readings.M_active_power.b": 1.9, "general_inspection.readings.M_active_power.c": 2.8, "general_inspection.readings.N_reactive_power.a": 0.3, "general_inspection.readings.N_reactive_power.b": 0.6, "general_inspection.readings.N_reactive_power.c": 0.5, "general_inspection.readings.O_apparent_power.a": 1.2, "general_inspection.readings.O_apparent_power.b": 1.8, "general_inspection.readings.O_apparent_power.c": 2.8, "general_inspection.readings.P_output_power.a": 17.0, "general_inspection.readings.P_output_power.b": 27.0, "general_inspection.readings.P_output_power.c": 40.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "All equipment is in good condition", "technician_name": "", "technician_id": 19898, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_NA_UPS_NA_2.pdf |  | {"station": "KLS", "date_time": "14/01/2023", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 28.0, "general_inspection.readings.B_module_temperature.max": 38.2, "general_inspection.readings.C_battery_run_time": 270.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 268.0, "general_inspection.readings.F_battery_voltage_v.negative": 263.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 234.0, "general_inspection.readings.I_rectifier_voltage.b": 233.0, "general_inspection.readings.I_rectifier_voltage.c": 235.0, "general_inspection.readings.J_bypass_voltage.a": 236.0, "general_inspection.readings.J_bypass_voltage.b": 334.0, "general_inspection.readings.J_bypass_voltage.c": 239.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 240.0, "general_inspection.readings.K_output_voltage.c": 240.0, "general_inspection.readings.L_output_current.a": 1.6, "general_inspection.readings.L_output_current.b": 4.7, "general_inspection.readings.L_output_current.c": 3.7, "general_inspection.readings.M_active_power.a": 0.4, "general_inspection.readings.M_active_power.b": 1.0, "general_inspection.readings.M_active_power.c": 0.8, "general_inspection.readings.N_reactive_power.a": 0.0, "general_inspection.readings.N_reactive_power.b": 0.2, "general_inspection.readings.N_reactive_power.c": 0.1, "general_inspection.readings.O_apparent_power.a": 0.3, "general_inspection.readings.O_apparent_power.b": 1.1, "general_inspection.readings.O_apparent_power.c": 0.8, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 15.0, "general_inspection.readings.P_output_power.c": 14.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.8, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.7, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": 200.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 100.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 100.0, "comments_recommendation": "all equipment in good conditions", "technician_name": "", "technician_id": 11727, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_NA_UPS_NA_1.pdf |  | {"station": "KLS", "date_time": "14/01/2022", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 24.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 240.0, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": 260.0, "general_inspection.readings.F_battery_voltage_v.negative": 261.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 271.0, "general_inspection.readings.I_rectifier_voltage.b": 272.0, "general_inspection.readings.I_rectifier_voltage.c": 273.0, "general_inspection.readings.J_bypass_voltage.a": 240.0, "general_inspection.readings.J_bypass_voltage.b": 241.0, "general_inspection.readings.J_bypass_voltage.c": 242.0, "general_inspection.readings.K_output_voltage.a": 1.5, "general_inspection.readings.K_output_voltage.b": 1.4, "general_inspection.readings.K_output_voltage.c": 1.3, "general_inspection.readings.L_output_current.a": 0.3, "general_inspection.readings.L_output_current.b": 1.2, "general_inspection.readings.L_output_current.c": 0.4, "general_inspection.readings.M_active_power.a": 0.3, "general_inspection.readings.M_active_power.b": 0.1, "general_inspection.readings.M_active_power.c": 0.9, "general_inspection.readings.N_reactive_power.a": 0.1, "general_inspection.readings.N_reactive_power.b": 0.1, "general_inspection.readings.N_reactive_power.c": 0.0, "general_inspection.readings.O_apparent_power.a": 0.2, "general_inspection.readings.O_apparent_power.b": 1.0, "general_inspection.readings.O_apparent_power.c": 1.0, "general_inspection.readings.P_output_power.a": 5.0, "general_inspection.readings.P_output_power.b": 14.0, "general_inspection.readings.P_output_power.c": 9.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": 12.6, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": 12.4, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": 12.4, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": null, "battery_backup_test.before.time_minutes": 240.0, "battery_backup_test.before.battery": 100.0, "battery_backup_test.after.time_minutes": 120.0, "battery_backup_test.after.battery": 50.0, "battery_backup_test.battery_backup_time": 120.0, "comments_recommendation": "OK", "technician_name": "", "technician_id": 7110, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_NA_UPS_NA (3).pdf |  | {"station": "KLS", "date_time": "2023-04-07T00:00:00", "safety_and_preparation.safety_precautions.status": true, "safety_and_preparation.inform_occ.status": true, "general_inspection.visual_inspection.status": true, "general_inspection.confirm_both_of_module_and_inverter.status": true, "general_inspection.record_reading.status": true, "general_inspection.readings.A_battery_capacity": 100.0, "general_inspection.readings.B_module_temperature.min": 65.0, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": 105.0, "general_inspection.readings.D_output_frequency": 50.0, "general_inspection.readings.E_bypass_frequency": 50.0, "general_inspection.readings.F_battery_voltage_v.positive": 268.0, "general_inspection.readings.F_battery_voltage_v.negative": 268.0, "general_inspection.readings.G_battery_charge_car.positive": 0.0, "general_inspection.readings.G_battery_charge_car.negative": 0.0, "general_inspection.readings.H_discharge_current": 0.0, "general_inspection.readings.I_rectifier_voltage.a": 254.0, "general_inspection.readings.I_rectifier_voltage.b": 254.0, "general_inspection.readings.I_rectifier_voltage.c": 255.0, "general_inspection.readings.J_bypass_voltage.a": 254.0, "general_inspection.readings.J_bypass_voltage.b": 254.0, "general_inspection.readings.J_bypass_voltage.c": 255.0, "general_inspection.readings.K_output_voltage.a": 240.0, "general_inspection.readings.K_output_voltage.b": 239.0, "general_inspection.readings.K_output_voltage.c": 239.0, "general_inspection.readings.L_output_current.a": 4.8, "general_inspection.readings.L_output_current.b": 7.6, "general_inspection.readings.L_output_current.c": 11.5, "general_inspection.readings.M_active_power.a": 1.1, "general_inspection.readings.M_active_power.b": 1.8, "general_inspection.readings.M_active_power.c": 2.0, "general_inspection.readings.N_reactive_power.a": 0.3, "general_inspection.readings.N_reactive_power.b": 0.5, "general_inspection.readings.N_reactive_power.c": 0.4, "general_inspection.readings.O_apparent_power.a": 1.1, "general_inspection.readings.O_apparent_power.b": 1.9, "general_inspection.readings.O_apparent_power.c": 2.7, "general_inspection.readings.P_output_power.a": 17.0, "general_inspection.readings.P_output_power.b": 28.0, "general_inspection.readings.P_output_power.c": 45.0, "servicing_and_cleaning.set_maintenance_bypass_mode.status": true, "servicing_and_cleaning.switch_on_maintenance_bypass.status": true, "servicing_and_cleaning.confirm_display_panel.status": true, "servicing_and_cleaning.switch_off_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_both_of_module.status": true, "servicing_and_cleaning.open_screw_and_pull_both_module.status": true, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": true, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": true, "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": true, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": true, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": true, "servicing_and_cleaning.button_on_off.status": true, "servicing_and_cleaning.normalized_all_battery_breakers.status": true, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": true, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": true, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": true, "servicing_and_cleaning.check_everything__normal.status": true, "battery_backup_test.check_battery_level.status": true, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": true, "battery_backup_test.turn_off_main_switch_breaker.status": true, "battery_backup_test.confirm_alarm_sounding.status": true, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": true, "battery_backup_test.switch_on_back_main_switch_breaker.status": true, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "good condition", "technician_name": "", "technician_id": 7223, "supervisor_name": "", "supervisor_id": 7111}
SC_PM_NA_UPS_NA_14.pdf |  | {"station": "OCC", "date_time": "", "safety_and_preparation.safety_precautions.status": null, "safety_and_preparation.inform_occ.status": null, "general_inspection.visual_inspection.status": null, "general_inspection.confirm_both_of_module_and_inverter.status": null, "general_inspection.record_reading.status": null, "general_inspection.readings.A_battery_capacity": null, "general_inspection.readings.B_module_temperature.min": null, "general_inspection.readings.B_module_temperature.max": null, "general_inspection.readings.C_battery_run_time": null, "general_inspection.readings.D_output_frequency": null, "general_inspection.readings.E_bypass_frequency": null, "general_inspection.readings.F_battery_voltage_v.positive": null, "general_inspection.readings.F_battery_voltage_v.negative": null, "general_inspection.readings.G_battery_charge_car.positive": null, "general_inspection.readings.G_battery_charge_car.negative": null, "general_inspection.readings.H_discharge_current": null, "general_inspection.readings.I_rectifier_voltage.a": null, "general_inspection.readings.I_rectifier_voltage.b": null, "general_inspection.readings.I_rectifier_voltage.c": null, "general_inspection.readings.J_bypass_voltage.a": null, "general_inspection.readings.J_bypass_voltage.b": null, "general_inspection.readings.J_bypass_voltage.c": null, "general_inspection.readings.K_output_voltage.a": null, "general_inspection.readings.K_output_voltage.b": null, "general_inspection.readings.K_output_voltage.c": null, "general_inspection.readings.L_output_current.a": null, "general_inspection.readings.L_output_current.b": null, "general_inspection.readings.L_output_current.c": null, "general_inspection.readings.M_active_power.a": null, "general_inspection.readings.M_active_power.b": null, "general_inspection.readings.M_active_power.c": null, "general_inspection.readings.N_reactive_power.a": null, "general_inspection.readings.N_reactive_power.b": null, "general_inspection.readings.N_reactive_power.c": null, "general_inspection.readings.O_apparent_power.a": null, "general_inspection.readings.O_apparent_power.b": null, "general_inspection.readings.O_apparent_power.c": null, "general_inspection.readings.P_output_power.a": null, "general_inspection.readings.P_output_power.b": null, "general_inspection.readings.P_output_power.c": null, "servicing_and_cleaning.set_maintenance_bypass_mode.status": null, "servicing_and_cleaning.switch_on_maintenance_bypass.status": null, "servicing_and_cleaning.confirm_display_panel.status": null, "servicing_and_cleaning.switch_off_all_battery_breakers.status": null, "servicing_and_cleaning.switch_off_both_of_module.status": null, "servicing_and_cleaning.open_screw_and_pull_both_module.status": null, "servicing_and_cleaning.open_battery_bank_and_check_voltage.status": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.status": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery1": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery2": null, "servicing_and_cleaning.wait_electrolytic_condensers_discharge.battery_readings.battery3": null, "servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries.status": "", "servicing_and_cleaning.check_end_to_end_batteries_voltages.status": null, "servicing_and_cleaning.do_the_cleaning_on_all_the_batteries.status": null, "servicing_and_cleaning.confirm_all_cables_after_cleaning.status": null, "servicing_and_cleaning.switch_on_both_module.status": null, "servicing_and_cleaning.button_on_off.status": null, "servicing_and_cleaning.normalized_all_battery_breakers.status": null, "servicing_and_cleaning.switch_off_switch_maintenance_bypass.status": null, "servicing_and_cleaning.set_the_ups_to_inverter_mode.status": null, "servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada.status": null, "servicing_and_cleaning.check_everything__normal.status": null, "battery_backup_test.check_battery_level.status": null, "battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated.status": null, "battery_backup_test.turn_off_main_switch_breaker.status": null, "battery_backup_test.confirm_alarm_sounding.status": null, "battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage.status": null, "battery_backup_test.switch_on_back_main_switch_breaker.status": null, "battery_backup_test.before.time_minutes": null, "battery_backup_test.before.battery": null, "battery_backup_test.after.time_minutes": null, "battery_backup_test.after.battery": null, "battery_backup_test.battery_backup_time": null, "comments_recommendation": "", "technician_name": "", "technician_id": "", "supervisor_name": "", "supervisor_id": ""}