## notification
notification_no | notification_type | notification_date | maintenance_plant | target_date | maint_work_centre | reported_by | work_order_no | assigned_to | parent_work_order_no | system_status | user_status | functional_location | location | superior_equipment | equipment | coding | work_request | description | tasks | staff_details | comments | object_part_items | cause_items | activity_items | approval.date_closed | approval.supervisor_verification
12408387 | M7 | 14/02/2025 | 0805 | 21/02/2025 | WS10 | IP1020250214 | 4000657933 |  |  | NOPR NOPT ORAS | REQ | PRAL-MRL-WS-TPS-MRLHTZ TPSS - Hang Tuah | WES Wayside Department |  |  | MRWSU001 I006 Inspection - 3 Months Interval | PM Inspection for Hang Tuah TPSS |  | [] | [] | PM Complete | [] | [] | [] | 21/02/2025 | 11858
12408894 | M7 | 15/02/2025 | 0805 | 22/02/2025 | WS10 | IP1020250215 | 4000658486 |  |  | NOPR NOPT ORAS OSTS | CLS ACK | PRAL-MRL-WS-TPS-MRLSSZ TPSS - Sultan Sulaiman | WES Wayside Department |  |  | MRWSU001 1006 Inspection - 3 Months Interval | PM Inspection for Sultan Sulaiman TPSS | - PM COMPLETE | ['1001'] | [{'staff_id': '10011858', 'name': 'NAZRULSHAH BIN MOHAMAD JUBERI', 'plan_start_date_&_time': '00/00/0000 00:00', 'plan_end_date_&_time': '00/00/0000 00:00', 'total': ''}] | All in good condition | ['TPSS'] | ['Scheduled maintenance'] | ['Check/Inspect -'] | 22/02/2025 | 11858

## work_order
work_order_no | work_order_type | date_opened | requester | target_date | cost_centre | notification_no | notification_type | priority | assigned_to | parent_work_order_no | maint_act_type | work_centre | maintenance_plant | functional_location | location | superior_equipment | equipment | description | operations | materials | labour_details | comments | object_part | cause | damage | action | approval.date_closed | approval.supervisor_verification
[6 empty] | 12408387 | [12 empty] | [] | [] | []
[19 empty] | [] | [] | []

## tpss_inspection_quarterly
workorder_id | tpss_location | inspection_date | 11kv_switchgear.incomer1.voltmeter | 11kv_switchgear.incomer1.ammeter | 11kv_switchgear.incomer1.protection_relay | 11kv_switchgear.incomer2.voltmeter | 11kv_switchgear.incomer2.ammeter | 11kv_switchgear.incomer2.protection_relay | 11kv_switchgear.rectifier_transformer.voltmeter | 11kv_switchgear.rectifier_transformer.ammeter | 11kv_switchgear.rectifier_transformer.protection_relay | 11kv_switchgear.service_transformer.voltmeter | 11kv_switchgear.service_transformer.ammeter | 11kv_switchgear.service_transformer.protection_relay | 750_dc_switchgear.rectifier_s/gear.voltage | 750_dc_switchgear.rectifier_s/gear.ampere | 750_dc_switchgear.rectifier_s/gear.status | battery_&_battery_charger.voltage | battery_&_battery_charger.ampere | main_switch_board.over_current_status.status | main_switch_board.over_current_status.remarks | power_equipment.rectifier | power_equipment.resistor_bank | overall_inspection.cleanliness | inspection_time.start_time | inspection_time.end_time | perform_by.name | perform_by.id | perform_by.date | verify_by.name | verify_by.date | reference_document | 750_dc_switchgear.rectifier_s/gear.protection_relay | 750_dc_switchgear.feeder1.ampere | 750_dc_switchgear.feeder1.status | 750_dc_switchgear.feeder1.protection_relay | 750_dc_switchgear.feeder2.ampere | 750_dc_switchgear.feeder2.status | 750_dc_switchgear.feeder2.protection_relay | 750_dc_switchgear.feeder3.ampere | 750_dc_switchgear.feeder3.status | 750_dc_switchgear.feeder3.protection_relay | 750_dc_switchgear.feeder4.ampere | 750_dc_switchgear.feeder4.status | 750_dc_switchgear.feeder4.protection_relay | 750_dc_switchgear.aaru.ampere | 750_dc_switchgear.aaru.status | 750_dc_switchgear.aaru.protection_relay | battery_&_battery_charger.terminal | battery_&_battery_charger.electrolyte_level | battery_&_battery_charger.charger_card | battery_&_battery_charger.ac_status | main_switch_board.earth_fault_relay_status.status | main_switch_board.earth_fault_relay_status.remarks | main_switch_board.indicator_light_status.status | main_switch_board.indicator_light_status.remarks | main_switch_board.voltmeter_reading.value | main_switch_board.voltmeter_reading.remarks | main_switch_board.ammeter_reading.value | main_switch_board.ammeter_reading.remarks | main_switch_board.cos_reading.value | main_switch_board.cos_reading.remarks | main_switch_board.remarks | power_equipment.rectifier_tx. | power_equipment.service_tx. | overall_inspection.lightings | overall_inspection.exhaust_fans | perform_by.technician | verify_by.id | verify_by.engineer/supervisor | filename
4000657933 | HANG TUAH | 21/02/2025 | 11.0 |  | NORMAL | 11.0 |  | NORMAL |  |  | NORMAL | 11.1 |  | NORMAL |  |  | NORMAL | 110 | 20 | NORMAL |  | NORMAL | NORMAL | OK | 03:00:00 | 04:00:00 | AMIRUL ASHRAFF | 20705 | 21/02/2025 | NAZRUL SHAH | 21/02/2025 | 1) 11KV SWITCHGEARS - 014273-38PM-1000 - K001, 2) 750V DC SWITCHGEAR (VOLUME 1~5) |  | 210 | FAULTY |  |  | FAULTY |  | 170 | FAULTY |  | 150 | FAULTY |  |  | NORMAL |  | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL |  | NORMAL |  | 415 |  | 50 |  | 0.90 |  |  | NORMAL | NORMAL | OK | OK | MAA | 11858 | NMJ | 4000657933
4000658486 | SSZ | 22/02/2025 | 11.2 |  | NORMAL | 11.3 |  | NORMAL |  |  | NORMAL | 11.3 |  | NORMAL |  |  |  | 125 | 6 | NORMAL |  | NORMAL | NORMAL | OK | 03:30:00 | 04:30:00 | AMIRUL ASHRAFF | 20705 | 22/02/2025 | NAZRUL SHAH | 22/02/2025 | 11KV SWITCHGEARS - 014273-38PM-1000 - K001, 750V DC SWITCHGEAR (VOLUME 1~5) | NORMAL |  | FAULTY | NORMAL |  | FAULTY | NORMAL |  | FAULTY | NORMAL |  | FAULTY | NORMAL |  |  | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL |  | NORMAL |  | 415 |  | 15 |  | 0.97 |  |  | NORMAL | NORMAL | OK | OK | MAA | 11858 | NMJ | 4000658486