## ups_system
workorder_id | filename | station | date_time | pm_order | checklist_items.safety_and_preparation.make_sure_safety_precautions_procedures_being_followed_as_required..status | checklist_items.safety_and_preparation.inform_occ_before_start_any_task..status | checklist_items.general_inspection.perform_visual_inspection_and_confirm_all_cable_properly_connected..status | checklist_items.general_inspection.confirm_both_of_module_is_on_and_inverter_mode..status | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.status | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.A_battery_capacity | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.B_module_temp.in | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.B_module_temp.out | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.C_battery_run_time | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.D_output_freq_hz | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.E_bypass_freq_hz | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.F_battery_voltage_v.positive | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.F_battery_voltage_v.negative | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.G_battery_charge_car_a.positive | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.G_battery_charge_car_a.negative | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.H_discharge_current_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.I_rectifier_voltage_v_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.I_rectifier_voltage_v_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.I_rectifier_voltage_v_c | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.J_bypass_voltage_v_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.J_bypass_voltage_v_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.J_bypass_voltage_v_c | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.K_output_voltage_v_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.K_output_voltage_v_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.K_output_voltage_v_c | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.L_output_current_a_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.L_output_current_a_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.L_output_current_a_c | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.M_active_power_kw_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.M_active_power_kw_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.M_active_power_kw_c | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.N_reactive_power_kva_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.N_reactive_power_kva_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.N_reactive_power_kva_c | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.O_apparent_power_kva_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.O_apparent_power_kva_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.O_apparent_power_kva_c | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.P_output_power_percent_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.P_output_power_percent_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.P_output_power_percent_c | checklist_items.servicing_and_cleaning.set_the_ups_to_maintenance_bypass_mode_by_using_command_from_module..status | checklist_items.servicing_and_cleaning.switching_on_switch_maintenance_bypass_in_front_of_ups_rack..status | checklist_items.servicing_and_cleaning.confirm_the_display_panel_is_showing_bypass_mode..status | checklist_items.servicing_and_cleaning.switch_off_all_battery_breakers..status | checklist_items.servicing_and_cleaning.switch_off_both_of_module_using_2_finger_push_button_on_off..status | checklist_items.servicing_and_cleaning.open_screw_and_pull_both_of_module_to_cleaning..status | checklist_items.servicing_and_cleaning.open_screws_each_battery_bank_and_check_the_voltage..status | checklist_items.servicing_and_cleaning.wait_for_the_electrolytic_condensers_on_the_power_board_to_discharge_wait_at_least_15min_before_proceed_any_maintenance_work..status | checklist_items.servicing_and_cleaning.h.battery_readings.battery1 | checklist_items.servicing_and_cleaning.h.battery_readings.battery2 | checklist_items.servicing_and_cleaning.h.battery_readings.battery3 | checklist_items.servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries._ensure_minimum_voltage_is_read_as_12v_and_maximum_should_not_be_more_than_13.8v..status | checklist_items.servicing_and_cleaning.j.status | checklist_items.servicing_and_cleaning.check_end_to_end_batteries_voltages..status | checklist_items.servicing_and_cleaning.do_the_cleaning_on_all_the_batteries._confirm_and_ensure_no_cable_is_disconnected_from_any_terminals..status | checklist_items.servicing_and_cleaning.m.status | checklist_items.servicing_and_cleaning.n.status | checklist_items.servicing_and_cleaning.after_completed_the_cleaning_confirm_all_cablings_are_secured_and_in_the_correct_position..status | checklist_items.servicing_and_cleaning.switch_on_both_of_module_using_2_finger_push_button_on_off..status | checklist_items.servicing_and_cleaning.button_on_off..status | checklist_items.servicing_and_cleaning.normalized_all_battery_breakers..status | checklist_items.servicing_and_cleaning.switch_off_switch_maintenance_bypass_in_front_of_ups_rack..status | checklist_items.servicing_and_cleaning.set_the_ups_to_inverter_mode_by_using_command_from_module..status | checklist_items.servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada..status | checklist_items.servicing_and_cleaning.check_and_see_is_everything_back_to_normal..status | checklist_items.battery_backup_test.before_proceed_this_test_make_sure_battery_level_should_be_above_80%_of_load..status | checklist_items.battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated..status | checklist_items.battery_backup_test.turn_off_main_switch_breaker_for_main_incoming_supply..status | checklist_items.battery_backup_test.confirm_after_a_few_seconds_alarm_sounding_"battery_working"_led_illuminate_and_ups_change_to_"battery_mode"..status | checklist_items.battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage..status | checklist_items.battery_backup_test.switch_on_back_main_switch_breaker_after_ups_reaching_50%_of_battery_level..status | checklist_items.battery_backup_test.battery_backup_test.before.time_minutes | checklist_items.battery_backup_test.battery_backup_test.before.battery_percentage | checklist_items.battery_backup_test.battery_backup_test.after.time_minutes | checklist_items.battery_backup_test.battery_backup_test.after.battery_percentage | checklist_items.battery_backup_test.battery_backup_test.battery_backup_time_minutes | comments_recommendation | performed_by.name | performed_by.id | verified_by.name | verified_by.id | reference_document
4000672868 | PS_PM_QTR_UPSSystem_4000672868.pdf | MAH | 16/04/2025 |  | TRUE | TRUE | TRUE | TRUE | [36 empty] | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE |  | TRUE | TRUE |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All in good condition | IZZUDDIN | 22388 | MOHD IRZAN | 7094 | KLMFEP-33001
4000672871 | PS_PM_QTR_UPSSystem_4000672871.pdf | MKU | 22/04/2025 |  | TRUE | TRUE |  | TRUE | TRUE | 100 | 37.9 |  | 261 | 50.06 | 50 | 268 | 249 | 0 | 0 | 0 | 233 | 234 | 237 | 235 | 264 | 237 | 239 | 240 | 240 | 1.4 | 4.3 | 3.6 | 0.3 | 0.2 | 0.2 | 0.3 | 1 | 0.9 | 0.3 | 1 | 0.9 | 4 | 15 | 14 |  |  |  | TRUE |  | TRUE | [7 empty] | TRUE | [5 empty] | TRUE | TRUE |  |  | TRUE | TRUE | [11 empty] | All in good condition | M. ISKANDAR | 20157 | NORIEZUWADI | 19234 | KLMFEP-33001
4000690941 | PS_PM_QTR_UPSSystem_4000690941.pdf | DCC | 26/07/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 98.7 | 25.5 | 27 |  | 50 | 50 | 268 | 267.4 | [6 empty] | 241.6 |  |  | 240.4 |  |  | 32 |  |  | 8.4 |  |  | 9.1 |  |  | 9 |  |  | 30.3 |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE |  | TRUE | TRUE |  |  | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | IN GOOD CONDITION | M. ISKANDAR | 20157 | NORIEZUWADI | 19234 | KLMFEP-33001
4000672874 | PS_PM_QTR_UPSSystem_4000672874.pdf | HAH | 17/04/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36 |  | 352 | 50 | 50 | 2.67 | 2.67 |  |  |  | 240 | 239 | 242 | 241 | 239 | 245 | 240 | 239 | 246 | 1.4 | 3.4 | 2.5 | 0.3 | 0.8 | 0.5 | 0 | 0.1 | 0.1 | 0.3 | 0.8 | 0.6 | 5 | 11 | 9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE |  | TRUE | TRUE |  |  | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All in good condition | IZZUDIN | 22388 | MOHD IRZAN | 7094 | KLMFEP-33001
4000673151 | PS_PM_QTR_UPSSystem_4000673151.pdf | OCC | 25/04/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 25.5 | 27 | 173 | 49.95 | 49.96 | 267.5 | 267.5 | 0 | 0.1 |  | 246.7 | 245.8 | 245.4 | 246.8 | 246 | 245.2 | 230 | 230 | 230 | 2.8 | 4.2 | 4.5 | 0.5 | 0.9 | 0.9 | 0.6 | 1 | 1.1 | 2.5 | 3.9 | 4 | 19.3 | 29 | 31.3 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE |  | TRUE | TRUE |  |  | TRUE |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | PM inspection already make by group Jurij and also tonight has test train so mainline remain ON. | SUFFI SHUKHAIRI | 20971 | JURIS | 19924 | KLMFEP-33001
4000673149 | PS_PM_QTR_UPSSystem_4000673149.pdf | TSA | 24/04/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 35.9 |  | 205 | 49.99 | 50 | 226 | 226 | 0 | 0 | 0 | 240 | 241 | 243 | 241 | 241 | 243 | 240 | 239 | 239 | 1.5 | 3.4 | 3.7 | 0.3 | 1.2 | 1.3 | 0.1 | 0.2 | 0.3 | 0 | 1.2 | 1.4 | 20 | 20 | 20 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE |  | TRUE | TRUE |  |  | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All in good condition | M.ISKANDAR | 20157 | NORIEZUWADI | 19234 | KLMFEP-33001
4000672877 | PS_PM_QTR_UPSSystem_4000672877.pdf | RAN | 2025-04-20 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 32.1 |  | 238 | 50.03 | 50 | 266 | 266 | 0 | 0 | 0 | 246 | 244 | 245 | 244 | 243 | 246 | 239 | 240 | 239 | 2.2 | 3.8 | 4.9 | 0.5 | 0.8 | 1.2 | 0 | 0.2 | 0.1 | 0.5 | 1 | 1.1 | 7 | 12 | 17 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE |  | TRUE | TRUE |  |  | TRUE |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All in good condition | IZZUDDIN | 22388 | MOHD IRZAN | 7094 | KLMFEP-33001
4000673152 | PS_PM_QTR_UPSSystem_4000673152.pdf | DCC | 26/04/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 50 | 50 | 50 | 26.8 | 26.8 | 0 | 0 | 0 | 242 | 242 | 245 | 242 |  |  | 240 |  |  | 38.8 | [5 empty] | 3.7 |  |  | 8.9 | [5 empty] | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE |  | TRUE | TRUE |  |  | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All in good condition | SUFFI SHUKHAIRI | 20971 | AHMAD JURIS | 19924
4000672878 | PS_PM_QTR_UPSSystem_4000672878.pdf | BAS | 21/04/2025 |  | TRUE | TRUE |  | TRUE | TRUE | 100 |  |  | 195 | 49.99 | 50 |  |  |  |  | 0 | 246 | 246 | 248 | 246 | 240 | 248 | 240 | 240 | 240 | 1.5 | 3.5 | 5.7 | 0.3 | 0.9 | 1.4 | 0 | 0.2 | 0.2 | 0.3 | 0.8 | 1.4 | 5 | 12 | 0.1 |  |  |  | TRUE |  | TRUE | [7 empty] | TRUE | [6 empty] | TRUE |  |  | TRUE | TRUE | [11 empty] | All in good condition |  | 20157 |  | 19234 | KLMFEP-33001
4000672876 | PS_PM_QTR_UPSSystem_4000672876.pdf | BNG | 19/04/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.6 |  | 600 | 50.04 | 50 | 266 | 266 | 0 | 0 | 0 | 243 | 243 | 246 | 244 | 243 | 246 | 239 | 239 | 240 | 2.3 | 6.2 | 4 | 0.5 | 1.5 | 0.3 | 0.2 | 0.2 | 0.1 | 0.6 | 1.5 | 0.3 | 9 | 25 | 13 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE |  | TRUE | TRUE |  |  | TRUE |  |  | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All in good condition | IZZUDDIN | 22388 | MOHD IRZAN | 7094 | KLMFEP-33001
4000672879 | PS_PM_QTR_UPSSystem_4000672879.pdf | CIT | 2025-04-23 |  | TRUE | TRUE |  | TRUE | TRUE | 100 |  |  | 451 | 49.98 | 80 |  |  |  |  | 0 | 246 | 245 | 245 | 246 | 245 | 245 | 239 | 240 | 239 | 0.8 | 1.7 | 2.2 | 0.1 | 0.3 | 0.7 | 0 | 0.4 | 0.1 | 0.1 | 0.4 | 0.2 | 0 | 5 | 11 |  |  |  | TRUE |  | TRUE | [7 empty] | TRUE | [6 empty] | TRUE |  |  | TRUE | TRUE | [11 empty] | All in good condition | ISKANDAR | 20157 | NORIEZUWADI | 19234 | KLMFEP-33001
4000673949 | PS_PM_QTR_UPSSystem_4000673949.pdf | TUN | 15/04/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  |  | 50.01 | 50.03 |  |  |  |  | 0 | 50 | 1 | 33 | 240 | 241 | 243 | 241 | 241 | 240 | 0.2 | 0.3 | 1.9 | 0.1 | 0.4 | 0.3 | 0.5 | 2 | 1.5 | 0.3 | 1 | 1 | 8.3 | 16.3 | 15.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE |  | TRUE | TRUE |  |  | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All in good condition | IZUDDIN | 22388 | MOHD IRZAN | 7094
4000675828 | PS_PM_QTR_UPSSystem_4000675828.pdf | KLS | 14/04/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 34.6 | 41.3 | 212 | 49.98 | 50 |  |  |  |  | 0 | 257 | 256 | 258 | 257 | 256 | 258 | 240 | 239 | 240 | 2.3 | 4.6 | 5.4 | 0.5 | 1 | 1.3 | 0.1 | 0.4 | 0.2 | 0.5 | 1 | 1.3 | 9 | 14 | 20 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE |  | TRUE | TRUE |  |  | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All in goud Condition | SHAHIN AMMAR | 20610 | DINESH | 7114 | KLMFEP-33001
4000672875 | PS_PM_QTR_UPSSystem_4000672875.pdf | IBI | 18/04/2025 |  | TRUE | TRUE |  | TRUE | [39 empty] | TRUE |  | TRUE | [7 empty] | TRUE |  |  |  | TRUE |  |  | TRUE |  | TRUE | TRUE | TRUE | [5 empty] | TRUE | [5 empty] | All in good conditon | IZZUDDIN | 22388 | MOHD IRZAN | 7094 | KLMFEP-33001
| SC_PM_NA_UPS_NA_1 (3).pdf | OCC | 27/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 26.6 | 32 | 180 | 50 | 50 | 267 | 268 |  |  | 0 | 247 | 247 | 247 | 247 | 247 | 245 | 230 | 230.9 | 230 |  | 3.5 | 4.3 | 2.3 | 2.9 | 3.4 | 6.6 | 0.7 | 1 | 0.6 | 0.7 | 1.2 | 0.03 | 0.89 | 0.84 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.3 | 13.3 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | UPS GOOD CONDITION |  | 7248 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_12.pdf | OCC | 27/07/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 629 |  |  | 267 | 267 |  |  |  | 250 | 249 | 249 | 251 | 249 | 248 | 231 | 231 | 231 | 13 | 14 | 17 | 2.9 | 3 | 3.8 | 1.1 | 1.3 | 1.7 | 3 | 3.4 | 3.1 | 23 | 25 | 31 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Battery run test in good condition |  | 20826 |  | 7110 | KLMFEP-33001
| SC_PM_NA_UPS_NA_2 (2).pdf | OCC | 27/04/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 26.6 | 32 | 180 | 50 | 50 | 267 | 268 | 0 | 0 | 0 | 247 | 247 | 247 | 247 | 247 | 245 | 230 | 230.9 | 230 | 2.3 | 3.5 | 4.3 | 2.3 | 2.9 | 3.4 | 0.6 | 0.7 | 1.1 | 0.6 | 0.7 | 1.2 | 0.03 | 0.89 | 0.84 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12 | 12 | 12 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 180 |  |  | 7248 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_3 (1).pdf | DCC | 26/07/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 |  |  | 50 | 50 | 272 | 272 |  |  | 0 | 246 | 245 | 247 | 246 | 246 | 246 | 240 | 240 | 240 | 37.7 | 40.1 | 36.7 | 7.7 | 7.6 | 8.1 | 8.7 | 8.6 | 8.8 | 96.4 | 98.6 | 102.3 |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [11 empty] | Cannot do battery run test due to battery cannot support high load equipment. | SYAZUAN | 19921 | MOHD RAZIF | 7222 | KLMFEP-33001
4000555059 | SC_PM_QTR_UPS_4000555059.pdf | DCC | 26/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 |  |  | 50 | 50 | 272 | 272 | 0 | 0 |  |  |  |  | 240 | 242 | 243 | 243 | 243 | 243 | 40 | 39 | 42 | [9 empty] | 5.7 | 8.7 | 8.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE |  | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [11 empty] | du not back up test, don't have spare batter, ups temporary in half condition, ups error battery faulty |  | 7248 |  | 7111 | KLMFEP-33001
4000493765 | SC_PM_QTR_UPS_4000493765.pdf | DCC | 26/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 26 |  |  | 50 | 50 | 272 | 272 | [6 empty] | 240 | 242 | 243 | 243 | 243 | 243 | 40 | 39 | 42 | [9 empty] | 8.7 | 8.7 |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.2 | 13.6 | 13.8 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | 100 | 20 | 50 | 20 | all equipment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
4000597742 | SC_PM_QTR_UPS_4000597742_1.pdf | DCC | 2024-01-26 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 |  |  |  |  | 272 | 272 | 0 | 0 |  |  |  |  | 245 |  |  | 228 |  |  | 39.5 | [14 empty] | TRUE | TRUE | [5 empty] | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | [6 empty] | TRUE | TRUE | TRUE |  | TRUE | [9 empty] | UPS in a good condition. I unit bateri voltage 25 | KARNA |  | AZHAR YUNUS | 7111 | KLMFEP-33001
4000555059 | SC_PM_QTR_UPS_4000555059_1.pdf | DCC | 26/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 |  |  | 50 | 50 | 272 | 271 | 0 | 0 |  |  |  |  | 240 | 242 | 243 | 243 | 243 | 243 | 40 | 39 | 42 | [9 empty] | 5.7 | 8.7 | 8.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | TRUE | [5 empty] | UPS error battery faulty do not backup tes, ups temporary in half in dition, dant have spare battery. |  | 7110 |  | 7111 | KLMFEP-33001
4000480679 | SC_PM_QTR_UPS_4000480679.pdf | DCC | 26/07/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 |  |  |  |  | 272 | 272 | [6 empty] | 242 |  |  | 239 |  |  | 39.7 | [14 empty] | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.2 | 13.4 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | 100 | 20 | 50 | 20 | not display time estimate | SYAHRUL AZWAN | 7110 | AZHAR YUNUS | 7111 | KLMFEP-33001
4000608031 | SC_PM_QTR_UPS_4000608031.pdf | DCC | 26/04/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 |  |  | 50 | 50 | 272 | 272 |  |  | 0 | 246 | 245 | 247 | 246 | 246 | 246 | 240 | 240 | 240 | 37.7 | 40.1 | 36.7 | 7.7 | 7.6 | 8.1 | 8.7 | 8.6 | 8.8 | 96.4 | 98.6 | 102.3 |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [11 empty] | cant do battery run test because battery cannot support high load equipment |  | 21048 |  | 7111 | KLMFEP-33001
4000530701 | SC_PM_QTR_UPS_4000530701.pdf | OCC | 26/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 |  | 180 | 50 | 50 | 267 | 267 | 0 | 0.1 | 0 |  |  |  | 247 | 247 | 246 | 230 | 230 | 230 | 24 | 29 | 5.2 | 0.5 | 0.6 | 1.1 | 0.6 | 0.7 | 1.2 | 0.6 | 0.7 | 1.2 | 0.83 | 0.89 | 0.83 | [8 empty] | 12 | 12 | 12 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 100 |  |  | 7222 |  | 7111 | KLMFEP-33001
4000467077 | SC_PM_QTR_UPS_4000467077.pdf | DCC | 26/04/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 40.1 | 38.8 | 349 | 19 | 50 | 267 | 268 | 0 | 0 | 0 | 298 | 248 | 247 | 230 | 227 | 277 | 5.3 | 5.5 | 1.3 | 1.2 | 1.2 | 2.3 | 0.3 | 0.1 | 0.4 | 0.3 | 0.1 | 0.4 | 1.2 | 1.2 | 2.2 | 19 | 10 | 37 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.6 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | 100 | 15 | 50 | 15 | not displaayed time astimate |  | 14952 |  | 7111 | KLMFEP-33001
4000669120 | SC_PM_QTR_UPS_4000669120.pdf | DCC | 26/01/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 50 | 50 | 50 | 268 | 268 | 0 | 0 | 0 | 242 | 242 | 245 | 242 |  |  | 240 |  |  | 38.5 |  |  | 8.6 |  |  | 3.7 |  |  | 8.9 | [5 empty] | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [10 empty] | KLMFEP-33001
4000597742 | SC_PM_QTR_UPS_4000597742.pdf | DCC | 26/01/2024 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | [5 empty] | 272 | 272 | 0 | 0 |  |  |  |  | 245 |  |  | 238 | [17 empty] | TRUE | [7 empty] | 13.5 | 13.8 | 25 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [6 empty] | TRUE | TRUE |  | TRUE | [9 empty] | Ups in a good condition. I unit bateri voltage 25V |  | 7262 |  | 7111 | KLMFEP-33001
4000509113 | SC_PM_QTR_UPS_4000509113.pdf | OCC | 26/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 |  |  | 50 | 50 | 272 | 272 | 0 | 0 |  |  |  |  | 240 | 242 | 243 | 243 | 243 | 243 | 4 | 3.9 | 4.2 | [9 empty] | 5.7 | 8.7 | 8.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.9 | 12.9 | 12.8 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | 100 | 20 | 50 | 20 | Good Condition |  | 7223 |  | 7111 | KLMFEP-33001
4000446356 | SC_PM_QTR_UPS_4000446356.pdf | DCC | 26/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 40.1 | 38.8 | 349 | 49 | 50 | 267 | 268 | 0 | 0 | 0 | 248 | 248 | 247 | 249 | 248 | 248 | 230 | 238 | 239 | 5.3 | 5.5 | 10.7 | 1.2 | 1.2 | 2.3 | 0.3 | 0.1 | 0.4 | 1.2 | 1.2 | 2.2 | 19 | 10 | 35 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.6 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | 100 | 15 | 50 | 15 | equitment in good conditions but not view or display estimate time back up, -battery drain out very fast |  | 11727 |  | 7111 | KLMFEP-33001
4000647402 | SC_PM_QTR_UPS_4000647402.pdf | OCC | 25/10/2024 | 4000647402 | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 21.0 | 23.3 |  |  |  | 267 | 267 | 0.1 | 0.1 |  | 246 | 245 | 245 | 247 | 246 | 244 | 231 | 231 | 231 | 11 | 13.1 | 19.3 | 2.2 | 2.7 | 4.1 | 2.5 | 3 | 4.5 | 1 | 1.1 | 1.6 | 18.5 | 23 | 34.1 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All battery in good condition: |  | 22153 |  | 7222 | KLMFEP-33001
4000576167 | SC_PM_QTR_UPS_4000576167.pdf | OCC | 25/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 26.6 | 32 | 180 | 50 | 50 | 267 | 268 | 0 | 0 | 0 | 247 | 247 | 244 | 247 | 247 | 245 | 230 | 230.9 | 230 | 2.8 | 3.5 | 4.3 | 2.3 | 2.9 | 3.4 | 0.6 | 0.7 | 1.1 | 0.6 | 0.7 | 1.2 | 0.03 | 0.89 | 0.84 |  | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | 13.5 | 13.3 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 195 | 100 | 15 |  |  | ups good Condition |  | 7262 |  | 7111 | KLMFEP-33001
4000493787 | SC_PM_QTR_UPS_4000493787.pdf | OCC | 25/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 32.5 |  | 180 | 49.9 | 49.97 | 247 | 247 | 0 | 0 | 0 |  |  |  | 247 | 246 | 245 | 230 | 230 | 230 | 2.4 | 3.1 | 5 | 0.5 | 0.6 | 0.2 | 2.1 | 2.8 | 4.2 |  |  |  | 0.8 | 0.9 | 0.9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.8 | 13 | 12.8 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 180 | all equipment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
4000615391 | SC_PM_QTR_UPS_4000615391.pdf | OCC | 25/07/2024 | 4000615391 | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 26.7 |  | 170 |  |  | 266 | 267 | 0 | 0 | 0 | 247 | 247 | 247 | 246 | 247 | 246 | 230 | 230 | 230 | 2.3 | 3.5 | 4.3 | 2.3 | 2.9 | 3.4 | 0.6 | 0.7 | 1.1 | 6.6 | 0.7 | 1.2 | 0.03 | 0.89 | 0.85 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | ups In good condition |  | 22278 |  | 7222 | KLMFEP-33001
4000555086 | SC_PM_QTR_UPS_4000555086.pdf | OCC | 25/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 |  | 180 | 80 | 50 | 267 | 267 | 0 | 0.1 | 0 | 347 | 247 | 244 | 247 | 247 | 246 | 230 | 230 | 230 | 2.4 | 2.9 | 1.1 | 0.6 | 0.7 | 1.2 | 0.6 | 0.7 | 1.2 | 0.6 | 0.7 | 1.2 | 0.83 | 0.84 | 0.83 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | - ups in good condition |  | 7110 |  | 7111 | KLMFEP-33001
4000608059 | SC_PM_QTR_UPS_4000608059.pdf | OCC | 25/04/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 629 |  |  | 267 | 267 |  |  |  | 250 | 249 | 249 | 251 | 249 | 248 | 231 | 231 | 231 | 13 | 14 | 17 | 2.9 | 3 | 3.8 | 1.1 | 1.3 | 1.7 | 3 | 3.4 | 3.1 | 23 | 25 | 31 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Battery run test in good condition. |  | 21048 |  | 7111 | KLMFEP-33001
4000530675 | SC_PM_QTR_UPS_4000530675.pdf | DCC | 25/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 |  |  | 50 | 50 | 272 | 272 | 0 | 0 |  |  |  |  | 240 | 242 | 243 | 243 | 243 | 243 | 40 | 39 | 42 | [9 empty] | 7.7 | 8.7 | 8.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.9 | 12.7 | 12.8 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | 100 | 20 | 50 | 20 |  |  | 7222 |  | 7111 | KLMFEP-33001
4000467097 | SC_PM_QTR_UPS_4000467097.pdf | OCC | 25/04/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 24.7 | 22.6 | 153 | 49.9 | 49.6 | 261 | 267 | 268 | 288 | 1.3 |  |  |  | 244 | 243 | 243 | 241 | 241 | 214 | 0.2 | 2.1 | 2.8 | 0.4 | 0.2 | 2.4 | 0.5 | 0.2 | 0.5 | 0.5 | 1.4 | 2.6 | 7 | 23 | 36 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.4 | 13.4 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 20 | 100 | 50 | 50 | 20 | ok |  | 14952 |  | 7111 | KLMFEP-33001
4000509061 | SC_PM_QTR_UPS_4000509061.pdf | OCC | 25/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 |  | 180 |  |  | 267 | 267 | 0 | 0.1 | 0 |  |  |  | 247 | 247 | 246 | 230 | 230 | 230 | 24 | 29 | 5.2 | 0.5 | 0.6 | 1.2 | 0.6 | 0.7 | 1.2 | 0.6 | 0.7 | 1.2 | 0.83 | 0.89 | 0.93 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12 | 12 | 12 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 180 | GOOD CONDITION |  | 7223 |  | 7111 | KLMFEP-33001
4000446335 | SC_PM_QTR_UPS_4000446335.pdf | OCC | 25/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 48.1 | 37.8 | 270 | 50 | 49.9 | 207 | 240 | 0 | 0 | 0 | 248 | 248 | 248 | 249 | 249 | 239 | 238 | 238 | 239 | 5.3 | 5.3 | 10.2 | 1.2 | 1.2 | 2.3 | 0.3 | 0.1 | 0.4 | 1.2 | 1.2 | 2.5 | 14 | 18 | 36 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.6 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 80 | all equitment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
4000480717 | SC_PM_QTR_UPS_4000480717.pdf | TSA | 24/04/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 42 |  | 185 |  |  | 212 | 268 | 0 | 0 | 0 | 238 | 237 | 240 | 238 | 239 | 240 | 240 | 241 | 244 | 1.6 | 1.5 | 4.4 | 0.3 | 1.2 | 1 | 0.1 | 0.1 | 0.2 | 0.4 | 1.3 | 1 | 5 | 17 | 15 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.6 | 13.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 90 | ok. | MOHD RAZIF | 7222 | AZHAR YUNUS | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA (7).pdf | TSA | 24/10/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 27.8 | 28.9 | 210 |  |  | 266 | 266 | 0 | 0 | 0 | 241 | 240 | 243 | 241 | 240 | 242 |  |  |  | 1.4 | 5.3 | 6 | 0.3 | 1.1 | 1.3 | 0.1 | 0.2 | 0.4 | 0.3 | 1.1 | 1.4 | 5 | 20 | 21 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipment are in good condition. |  | 20005 |  | 7248 | KLMFEP-33001
4000576188 | SC_PM_QTR_UPS_4000576188.pdf | TSA | 24/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.0 | 39.1 | 228 | 50.04 | 50 | 266 | 266 | 0 | 0 | 0 | 234 | 236 | 237 | 234 | 236 | 237 | 240 | 239 | 240 | 1.2 | 4.2 | 5.4 | 0.3 | 1 | 1.2 | 0 | 0 | 0.3 | 0.3 | 1 | 1.2 | 4 | 14 | 20 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | 100 |  |  | 228 | All Good Condition |  | 7262 |  | 7111 | KLMFEP-33001
4000509052 | SC_PM_QTR_UPS_4000509052.pdf | TSA | 24/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 | 33 | 207 | 50 | 50 | 266 | 266 | 0 | 0 | 0 | 237 | 238 | 240 | 237 | 238 | 240 | 240 | 239 | 240 | 1 | 4.8 | 6.2 | 0.2 | 1.3 | 1.4 | 0.1 | 0.1 | 0.3 | 0.2 | 1.2 | 1.4 | 3 | 19 | 21 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.5 | 12.8 | 12.8 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 180 | 2 batery faulty and all equipment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_9.pdf | TSA | 24/07/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.7 | 40.2 | 210 |  |  | 266 | 266 | 0 | 0 | 0 | 237 | 239 | 240 | 237 | 239 | 24 |  |  |  | 1.3 | 4.5 | 5.6 | 0.3 | 1.1 | 1.3 | 0 | 0 | 0.3 | 0.3 | 1.1 | 1.3 | 4 | 17 | 20 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 53.7 | 53.6 | 53.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Battery & Module in good condition. |  | 19921 |  | 7222 | KLMFEP-33001
4000555036 | SC_PM_QTR_UPS_4000555036.pdf | BAS | 24/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.5 | 38.4 | 225 | 50 | 50 | 266 | 266 | 0 | 0 | 0 | 249 | 249 | 249 | 249 | 249 | 260 | 240 | 240 | 240 | 1.5 | 3.8 | 6 | 0.3 | 0.8 | 1.4 | 0 | 0 | 0.2 | 1.3 | 0.8 | 1.4 | 5 | 12 | 32 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [7 empty] | 7222 |  | 7111 | KLMFEP-33001
4000555099 | SC_PM_QTR_UPS_4000555099.pdf | TSA | 24/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 32.7 | 39.3 | 235 | 50 | 50 | 266 | 206 | 0 | 0 | 0 | 235 | 236 | 237 | 240 | 239 | 240 | 1.4 | 4.8 | 5.1 | 0.3 | 1 | 1.2 | 0 | 0.1 | 0.3 | 0 | 0.1 | 0.3 | 0.3 | 1 | 1.2 | 5 | 15 | 18 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All batery in good condition. connection cable and inficator module good condition |  | 7110 |  | 7111 | KLMFEP-33001
4000480715 | SC_PM_QTR_UPS_4000480715.pdf | TSA | 24/07/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.9 | 40.5 | 290 |  |  | 266 | 266 | 0 | 0 | 0 | 240 | 241 | 243 | 240 | 241 | 242 | 240 | 239 | 240 | 1 | 4.1 | 4.9 | 0.2 | 1 | 1.1 | 0 | 0 | 0.2 | 0.2 | 1 | 1.2 | 4 | 16 | 17 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.4 | 13.3 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 540 | 100 |  |  |  | ups faulty\alarm battery discharge appear\must battery broken emporary maintanance bypass | SYAHRUL AZWAN | 7110 | AZHAR YUNUS | 7111 | KLMFEP-33001
4000608074 | SC_PM_QTR_UPS_4000608074.pdf | TSA | 2024-04-24 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 33.7 | 40.1 | 218 |  |  | 266 | 266 | 0 | 0 | 0 | 236 | 239 | 241 | 236 | 239 | 241 | 240 | 239 | 240 | 1.6 | 5.5 | 6.1 | 0.3 | 1.3 | 1.3 | 0.1 | 0.1 | 0.3 | 0.4 | 1.2 | 1.3 | 5 | 20 | 21 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | -Hardware In good condition |  | 20079 |  | 7111 | KLMFEP-33001
4000530710 | SC_PM_QTR_UPS_4000530710.pdf | TSA | 24/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28.0 | 33.0 | 196.2 |  |  | 266 | 266 | 0 | 0.6 | 0 | 237 | 238 | 240 | 237 | 238 | 260 | 240 | 259 | 240 | 1 | 4.8 | 6.2 | 0.2 | 1.2 | 1.7 | 0.1 | 0.1 | 0.3 | 0.2 | 1.2 | 1.4 | 3 | 19 | 21 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.5 |  | 12.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 180 | good Condition |  | 7110 |  | 7111 | KLMFEP-33001
4000668040 | SC_PM_QTR_UPS_4000668040.pdf | TSA | 24/01/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 29.9 | 35.9 | 204 |  |  | 266 | 266 | 0 | 0 | 0 | 239 | 241 | 243 | 240 | 241 | 243 | 240 | 239 | 239 | 1.5 | 5.5 | 6.2 | 0.3 | 1.2 | 1.4 | 0.1 | 0.2 | 0.4 | 0.3 | 1.1 | 1.4 | 5 | 20 | 21 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | UPS IN GOOD CONDITION |  | 22876 |  | 7110 | KLMFEP-33001
4000597870 | SC_PM_QTR_UPS_4000597870.pdf | TSA | 24/01/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.0 | 39.1 | 228 | 50.04 | 50 | 266 | 266 | 0 | 0 | 0 | 234 | 236 | 237 | 234 | 236 | 237 | 240 | 239 | 240 | 1.2 | 4.3 | 5.4 | 0.3 | 1 | 1.2 | 0 | 0 | 0.3 | 0.3 | 1 | 1.2 | 4 | 14 | 20 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All good condition |  | 7248 |  | 7111 | KLMFEP-33001
4000509053 | SC_PM_QTR_UPS_4000509053.pdf | TSA | 24/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28.0 | 33.0 | 207 |  |  | 266 | 266 | 0 | 0 | 0 | 237 | 238 | 240 | 237 | 238 | 240 | 240 | 239 | 240 | 1.07 | 48 | 6.2 | 0.2 | 1.3 | 1.4 | 0.1 | 0.1 | 0.3 | 0.2 | 1.2 | 1.4 | 3 | 19 | 21 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.5 | 12.7 | 12.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 180 | Good Condition |  | 7223 |  | 7111 | KLMFEP-33001
4000446312 | SC_PM_QTR_UPS_4000446312.pdf | TSA | 24/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 42 |  | 185 | 30 | 50 | 272 | 268 | 0 | 0 | 0 | 238 | 237 | 240 | 238 | 239 | 240 | 240 | 241 | 244 | 1.6 | 1.3 | 4.4 | 0.3 | 1.2 | 1 | 0.1 | 0.1 | 0.2 | 0.4 | 1.3 | 1 | 5 | 17 | 15 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.6 | 13.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 200 | 100 | 110 | 80 | 110 | all equitment in good conditions. |  |  |  | 7111 | KLMFEP-33001
4000480674 | SC_PM_QTR_UPS_4000480674.pdf | CIT | 2023-07-23 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 30 | 37.9 | 383 |  |  | 266 | 268 | 0 | 0 | 0 | 239 | 240 | 241 | 240 | 239 | 241 | 240 | 239 | 239 | 240 | 239 | 239 | 1.1 | 1.9 | 3.9 | 0.2 | 0.5 | 0.9 | 0.1 | 0 | 0.1 | 0.2 | 0.5 | 0.9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.7 | 13.5 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 380 | 100 | 180 | 50 | 150 | Ok | SYAHRUL AZWAN | 7110 | AZHAR YUNUS | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_7.pdf | CIT | 23/11/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 30.2 | 34.5 | 377 |  |  | 266 | 268 | 0 | 0.1 | 0 | 245 | 243 | 246 | 245 | 243 | 247 |  |  |  | 1.2 | 2 | 3.9 | 0.2 | 0.5 | 0.9 | 0.1 | 0.1 | 0.1 | 0.3 | 0.4 | 0.9 | 4 | 7 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | ALL EQUIPMENTS ARE IN GOOD CONDITION |  | 21970 |  | 7223 | KLMFEP-33001
4000646748 | SC_PM_QTR_UPS_4000646748.pdf | CIT | 23/10/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 34.5 | 37.5 | 379 |  |  | 266 | 268 | 0 | 0.1 | 0 | 299 | 248 | 250 | 299 | 247 | 250 | 240 | 239 | 239 | 1.2 | 1.9 | 3.6 | 0.2 | 0.5 | 0.8 | 0.1 | 0.1 | 0.1 | 0.2 | 0.5 | 0.9 | 4 | 6 | 13 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | replace for unit new battery-madule in good condition |  | 19925 |  | 7256 | KLMFEP-33001
4000576119 | SC_PM_QTR_UPS_4000576119.pdf | CIT | 23/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 38 |  | 365 | 50.03 | 50 | 266 | 268 | 0 | 0.1 | 0 | 250 | 249 | 250 | 250 | 249 | 251 | 239 | 239 | 239 | 1.3 | 2 | 3.9 | 0.2 | 0.4 | 0.9 | 0.1 | 0.1 | 0.2 | 0.3 | 0.5 | 0.9 | 4 | 6 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Time For both module not same Module 1 2h 25m and module 2 6h 5m |  | 7110 |  | 7111 | KLMFEP-33001
4000493761 | SC_PM_QTR_UPS_4000493761.pdf | CIT | 23/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28.5 | 35.0 | 376 |  |  | 266 | 268 | 0 | 0.1 | 0 | 248 | 247 | 245 | 248 | 247 | 249 | 240 | 240 | 239 | 1.1 | 2.1 | 4.1 | 0.2 | 0.4 | 0.9 | 0 | 1 | 0 | 0.2 | 0.4 | 0.9 | 4 | 6 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.8 | 12.7 | 12.8 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 380 | 100 | 180 | 50 | 180 | all equipment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
4000660367 | SC_PM_QTR_UPS_4000660367.pdf | CIT | 2025-01-23 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 27.7 | 33.8 | 377 |  |  | 266 | 268 | 0 | 0.1 | 0 | 246 | 245 | 247 | 246 | 245 | 248 | 239 | 239 | 239 | 1.1 | 2.2 | 3.6 | 0.2 | 0.4 | 0.8 | 1 | 0 | 0.1 | 0.3 | 0.4 | 0.8 | 4 | 7 | 13 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | UPS in a good condition. |  | 22777 |  | 7222 | KLMFEP-33001
4000555052 | SC_PM_QTR_UPS_4000555052.pdf | CIT | 23/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 110 | 37 |  | 165 | 50 | 50 | 272 | 272 | 0 | 0 | 0 | 244 |  |  | 244 | 243 | 244 | 239 | 239 | 239 | 2.6 | 6.2 | 6.8 | 0.6 | 1.3 | 1.6 | 0 | 0.1 | 0.2 | 0.6 | 1.2 | 1.7 | 9 | 19 | 25 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [7 empty] | 7222 |  | 7111 | KLMFEP-33001
4000608023 | SC_PM_QTR_UPS_4000608023.pdf | CIT | 23/04/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28.2 | 34.9 | 369 | 50.4 | 50 | 266 | 268 | 0 | 0.1 | 0 | 249 | 248 | 250 | 249 | 248 | 250 | 240 | 239 | 239 | 1.3 | 1.8 | 3.9 | 0.3 | 0.4 | 0.9 | 0.1 | 0.1 | 0.2 | 0.3 | 0.4 | 0.9 | 5 | 6 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | (D01-D10) 1 battery faulty |  | 21048 |  | 7111 | KLMFEP-33001
4000530672 | SC_PM_QTR_UPS_4000530672.pdf | CIT | 23/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28.5 | 35.0 | 375 |  |  | 266 | 268 | 0.8 | 0.1 | 0 | 248 | 247 | 245 | 248 | 247 | 249 | 240 | 240 | 235 | 1.1 | 2.1 | 4.1 | 0.2 | 0.4 | 0.9 | 0.1 | 1 | 0.1 | 0.2 | 0.4 | 0.9 | 4 | 6 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.5 | 12.6 | 12.8 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 81 | 100 | 180 | 10 | 180 | Good Condition |  | 7110 |  | 7111 | KLMFEP-33001
4000467073 | SC_PM_QTR_UPS_4000467073.pdf | CIT | 23/04/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 37.1 | 44.8 | 307 |  |  | 268 | 268 | 0 | 0.1 | 0 | 242 | 242 | 249 | 248 | 249 | 240 | 241 | 239 | 239 | 1 | 2 | 3 | 0.2 | 0.4 | 0.7 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.7 | 3 | 2 | 11 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.4 | 13.2 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 160 | 100 | 80 | 50 | 80 | ok |  | 7222 |  | 7111 | KLMFEP-33001
4000597714 | SC_PM_QTR_UPS_4000597714.pdf | CIT | 23/01/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 35.4 | 42.5 | 169 | 50.05 | 50 | 272 | 266 | 0 | 0 | 0 | 246 | 246 | 248 | 247 | 246 | 248 | 240 | 240 | 240 | 2.6 | 5.7 | 7.3 | 0.6 | 1.4 | 1.6 | 0 | 0.1 | 0.2 | 0.6 | 1.3 | 1.7 | 10 | 18 | 24 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All EQUIPMENT IN A GOOD CONDITION |  | 7248 |  | 7111 | KLMFEP-33001
4000509117 | SC_PM_QTR_UPS_4000509117.pdf | CIT | 23/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28.5 | 35.0 | 375 |  |  | 266 | 268 | 0.8 | 0.1 | 0 | 248 | 247 | 245 | 248 | 247 | 244 |  |  |  | 1.1 | 2.1 | 4.1 | 2 | 0.4 | 0.9 | 0.1 | 10 | 0.1 | 0.2 | 0.4 | 0.9 | 4 | 6 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.5 | 12.6 | 12.8 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 180 | 50 | 180 |  |  | 7223 |  | 7111 | KLMFEP-33001
4000446359 | SC_PM_QTR_UPS_4000446359.pdf | CIT | 23/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 37.1 | 44.8 | 307 | 50 | 50 | 268 | 269 | 0 | 0.1 | 0 | 240 | 248 | 249 | 248 | 249 | 240 | 240 | 239 | 239 | 1 | 2 | 3 | 0.2 | 0.4 | 0.7 | 0.1 | 0 | 0.1 | 0.2 | 0.4 | 0.7 | 3 | 2 | 11 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.4 | 13.2 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 120 | 100 | 60 | 50 | 120 | ok |  | 7223 |  | 7111 | KLMFEP-33001
4000509068 | SC_PM_QTR_UPS_4000509068.pdf | MKU | 22/04/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36.6 | 42.6 | 306 |  |  | 262 | 262 | 0 | 0 | 0 | 243 | 242 | 244 | 243 | 242 | 244 | 240 | 240 | 240 | 1.4 | 3.3 | 3.6 | 0.3 | 0.7 | 0.78 | 0 | 0.1 | 0.2 | 0.3 | 0.8 | 0.8 | 5 | 12 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.4 | 12.6 | 12.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 160 | 100 | 80 | 150 | 80 | ok |  | 7222 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_1 (4).pdf | Mku | 22/11/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 37.3 |  | 238 | 50.04 | 50 | 268 | 268 | 0 | 0 | 0 | 238 | 238 | 239 | 238 | 238 | 239 | 239 | 239 | 240 | 1.6 | 5.3 | 3.8 | 0.3 | 1.2 | 1 | 0 | 0.3 | 0.2 | 0.3 | 1.2 | 0.9 | 5 | 19 | 15 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | ALL EQUIPMENT IN GOOD CONDITION |  | 7248 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_2 (3).pdf | MKU | 22/10/2024 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 32.5 |  | 259 | 50.05 | 50 | 268 | 268 | 0 | 0 | 0 | 237 | 236 | 238 | 237 | 237 | 239 | 240 | 240 | 239 | 1.6 | 4.4 | 3.7 | 0.3 | 1.1 | 0.8 | 0 | 0.2 | 0.1 | 0.4 | 1 | 1.8 | 5 | 16 | 12 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All battery in good condition and perform very well. |  | 11727 |  | 7256 | KLMFEP-33001
| SC_PM_NA_UPS_NA_3.pdf | Mku | 22/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 260 | 50 | 50 | 268 | 269 | 0 | 0 | 0 | 239 | 240 | 241 | 240 | 231 | 241 | 234 | 240 | 241 | 1.6 | 4.7 | 3.7 | 0.4 | 1 | 0.8 | 0 | 0.2 | 0.1 | 0.3 | 1.1 | 0.8 | 5 | 15 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | -all equipment in good condition -all cable tigth and secure |  | 7119 |  | 7111 | KLMFEP-33001
4000509070 | SC_PM_QTR_UPS_4000509070.pdf | MKU | 22/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.3 | 38.2 | 241 | 50 | 50 | 268 | 268 | 0 | 0 | 0 | 234 | 233 | 235 | 234 | 233 | 235 | 240 | 240 | 240 | 1.6 | 4.7 | 3.7 | 0.4 | 1 | 0.8 | 0 | 0.2 | 0.1 | 0.3 | 1.1 | 0.8 | 5 | 15 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.4 | 13.5 | 13.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 240 | 100 | 100 | 80 | 100 | Good Condition |  | 7223 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA (6).pdf | MKU | 22/07/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 29 | 33.5 | 265 |  |  | 26.9 | 26.9 | 0 | 0 | 0 | 237 | 236 | 240 | 237 | 236 | 240 |  |  |  | 1.45 | 4.5 | 3.5 | 0.3 | 1 | 0.8 | 0 | 0.2 | 0.1 | 0.3 | 1 | 0.8 | 5 | 17 | 13 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All batteries in good condition. |  | 22153 |  | 7223 | KLMFEP-33001
| SC_PM_NA_UPS_NA_2 (1).pdf | MKU | 22/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.3 | 38.2 | 260 | 50 | 50 | 218 | 268 | 0 | 0 | 0 | 234 | 233 | 235 | 234 | 233 | 235 | 240 | 240 | 240 | 1.6 | 4.7 | 3.7 | 0.4 | 1 | 0.8 | 0 | 0.2 | 0.1 | 0.3 | 1.1 | 0.8 | 5 | 15 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [7 empty] | 7222 |  | 7111 | KLMFEP-33001
4000509069 | SC_PM_QTR_UPS_4000509069.pdf | MKU | 22/07/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.2 | 37.9 | 247 | 50 | 50 | 265 | 269 | 0 | 0 | 0 | 237 | 237 | 239 | 237 | 236 | 234 | 240 | 240 | 239 | 1.6 | 4.5 | 3.7 | 0.3 | 1 | 0.9 | 0 | 0.2 | 0.1 | 0.3 | 1.1 | 0.8 | 5 | 16 | 12 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.6 | 13.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 240 | 100 | 100 | 50 | 200 | all equitment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_1 (5).pdf | MKU | 22/04/2024 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 22.5 | 23.8 | 238 | 50.03 |  | 268 | 268 | 0 | 0 | 0 | 240 | 236 | 242 | 240 | 238 | 242 |  |  |  | 1.6 | 5.1 | 4.3 | 0.3 | 1 | 0.8 | 0 | 0.4 | 0.4 | 0.3 | 1.2 | 1 | 5 | 18 | 15 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All batteries and module in good condition. |  | 19921 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA (2).pdf | MKU | 22/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.3 | 38.2 | 240 |  |  | 268 | 268 | 0 | 0 | 0 | 234 | 233 | 235 | 234 | 233 | 235 | 240 | 240 | 240 | 1.6 | 4.7 | 3.1 | 0.4 | 1 | 0.3 | 0 | 0.8 | 0.1 | 0.3 | 1.1 | 0.8 | 5 | 15 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.4 | 13.5 | 13.5 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 200 | 100 | 100 | 150 | 100 |  |  | 7110 |  | 7111 | KLMFEP-33001
4000669552 | SC_PM_QTR_UPS_4000669552.pdf | MKU | 22/01/2025 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 28.6 | 35.1 | 246 |  |  | 269 | 269 | 0 | 0 | 0 | 235 | 234 | 236 | 235 | 234 | 236 | 240 | 239 | 239 | 1.6 | 4.4 | 3.6 | 0.3 | 1 | 0.8 | 0.1 | 0.2 | 0.2 | 0.9 | 1 | 0.9 | 5 | 15 | 13 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | UPS in a good condition. |  | 22776 |  | 7222 | KLMFEP-33001
4000509072 | SC_PM_QTR_UPS_4000509072.pdf | Mku | 22/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.3 | 34.2 | 240 |  |  | 269 | 268 | 0 | 0 | 0 | 234 | 233 | 235 | 234 | 233 | 235 | 240 | 240 | 240 | 1.6 | 4.7 | 3.7 | 0.4 | 1.1 | 0.8 | 0 | 0.2 | 0.1 | 0.3 | 1.1 | 0.8 | 5 | 15 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.4 | 13.5 | 13.5 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 200 | 100 | 100 | 50 | 100 |  |  | 7222 |  | 7111 | KLMFEP-33001
4000509067 | SC_PM_QTR_UPS_4000509067.pdf | MKU | 22/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36.6 | 42.6 | 310 |  |  | 262 | 262 | 0 | 0 | 0 | 243 | 242 | 244 | 243 | 242 | 244 | 240 | 240 | 240 | 1.4 | 3.3 | 3.6 | 0.3 | 0.7 | 0.8 | 0 | 0.1 | 0.2 | 0.3 | 0.8 | 0 | 5 | 12 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.4 | 12.6 | 12.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 160 | 100 | 80 | 50 | 80 | OK |  | 7223 |  | 7111 | KLMFEP-33001
4000576104 | SC_PM_QTR_UPS_4000576104.pdf | BAS | 21/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 250 | 50.03 | 50 | 266 | 266 | 0 | 0 | 0 | 247 | 248 | 250 | 247 | 248 | 250 | 239 | 240 | 240 | 1.4 | 3.6 | 5.5 | 0.3 | 0.8 | 1.3 | 0 | 0.2 | 0.2 | 0.3 | 0.7 | 1.3 | 3 | 12 | 20 |  |  |  | TRUE | TRUE | TRUE | [30 empty] | All equipment in good condition |  | 20160 |  | 7111 | KLMFEP-33001
4000493753 | SC_PM_QTR_UPS_4000493753.pdf | BAS | 21/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.5 | 38.4 | 207 | 50 | 50 | 266 | 266 | 0 | 0 | 0 | 249 | 249 | 249 | 249 | 249 | 251 | 240 | 240 | 240 | 1.5 | 3.8 | 6 | 0.3 | 0.8 | 1.4 | 0 | 0 | 0.3 | 0.3 | 0.8 | 1.4 | 5 | 12 | 22 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.6 | 13.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 190 | 100 | 100 | 50 | 100 | Good Condition. | ROHIZAN | 7223 | AZHAR YUNUS | 7111 | KLMFEP-33001
4000597702 | SC_PM_QTR_UPS_4000597702.pdf | BAS | 21/01/2024 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 31.8 | 38.3 | 219 | 50 | 50 | 266 | 266 | 0 | 0 | 0 | 249 | 248 | 252 | 249 | 248 | 252 | 240 | 240 | 241 | 1.5 | 4.1 | 6 | 0.3 | 0.9 | 1.4 | 0 | 0.1 | 0.2 | 0.3 | 0.9 | 1.5 | 5 | 14 | 23 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | * Battery bank 1 and 2 (A01-040) need to be replaced. * Battery is damaged. * Battery can only cover 93% * Module P02 need to calibrate. |  | 20079 |  |  | KLMFEP-33001
| SC_PM_NA_UPS_NA_1 (6).pdf | BAS | 21/07/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28.3 | 32.9 | 268 |  |  | 266 | 266 | 0 | 0 | 0 | 248 | 247 | 252 | 248 | 247 | 252 |  |  |  | 1.3 | 2.9 | 5.1 | 0.3 | 0.6 | 1.1 | 0 | 0.1 | 0.1 | 0.3 | 0.7 | 1.1 | 4 | 11 | 17 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipment are in good condition. |  | 20005 |  | 7223 | KLMFEP-33001
4000480661 | SC_PM_QTR_UPS_4000480661.pdf | BAS | 21/07/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.3 | 38.3 | 228 |  |  | 266 | 206 | 0 | 0 | 0 | 249 | 249 | 249 | 249 | 249 | 252 | 240 | 240 | 240 | 1.5 | 3.8 | 6 | 3 | 9 | 1.4 | 0 | 0 | 0.3 | 0.3 | 0.8 | 1.4 | 5 | 13 | 22 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.6 | 13 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 190 | 100 | 100 | 50 | 100 | all equipment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
4000530660 | SC_PM_QTR_UPS_4000530660.pdf | BAS | 2023-04-21 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.5 | 38.4 | 225 |  |  | 266 | 266 | 0 | 0 | 0 | 249 | 249 | 249 | 249 | 249 | 250 | 240 | 240 | 240 | 1.5 | 3.8 | 6 | 0.3 | 0 | 1.4 | 0 | 0 | 0.3 | 0.3 | 0 | 1.4 | 5 | 12 | 22 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.6 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 200 | 100 | 100 | 50 | 100 |  |  | 7110 |  | 7111 | KLMFEP-33001
4000608011 | SC_PM_QTR_UPS_4000608011.pdf | BAS | 21/04/2024 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 33.1 |  | 238 | 50.03 | 50 | 266 | 266 | 0 | 0 | 0 | 249 | 248 | 251 | 248 | 249 | 252 | 240 | 239 | 240 | 1.5 | 3.4 | 5.6 | 0.3 | 0.8 | 1.3 | 0 | 0.1 | 0.2 | 0.3 | 0.8 | 1.4 | 5 | 12 | 20 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All module and batteries in good condition. Only using bank 3, bank 1 and 2 temporary doesn't have batteries due expired batteries. |  | 19921 |  | 7111 | KLMFEP-33001
4000467064 | SC_PM_QTR_UPS_4000467064.pdf | BAS | 21/04/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 29.3 | 36.6 | 272 |  |  | 267 | 268 | 1 | 0 | 0 | 248 | 248 | 250 | 248 | 248 | 254 | 240 | 240 | 240 | 1.5 | 3.5 | 4.5 | 0.3 | 0.7 | 1 | 0 | 0.1 | 0.1 | 0.3 | 0 | 1 | 8 | 11 | 16 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 120 | 12.9 | 13.2 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 80 | 50 | 80 | ok |  | 7110 |  | 7111 | KLMFEP-33001
4000660989 | SC_PM_QTR_UPS_4000660989.pdf | BAS | 21/01/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.1 | 39.8 | 243 |  |  | 266 | 266 | 0 | 0 | 0 | 246 | 247 | 249 | 246 | 246 | 249 | 241 | 230 | 240 | 1.4 | 3.1 | 5.6 | 0.3 | 0.7 | 0.2 | 0 | 0.2 | 0.1 | 0.3 | 0.8 | 1.3 | 5 | 12 | 19 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | # UPS in a good condition |  | 2276 |  | 7222 | KLMFEP-33001
4000509125 | SC_PM_QTR_UPS_4000509125.pdf | BAS | 21/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.5 | 38.4 | 225 | 50 | 50 | 266 | 266 | 0 | 0 | 0 | 249 | 249 | 249 | 249 | 249 | 250 | 240 | 240 | 240 | 1.5 | 3.8 | 6 | 0.3 | 0.8 | 1.4 | 0 | 0 | 0.3 | 0.3 | 0.8 | 1.4 | 5 | 12 | 22 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.6 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 200 | 100 | 100 | 50 | 100 |  |  | 7222 |  | 7111 | KLMFEP-33001
4000446126 | SC_PM_QTR_UPS_4000446126.pdf | BAS | 21/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 29.6 | 36.6 | 272 | 80 | 50 | 269 | 269 | 0 | 0 | 0 | 248 | 248 | 250 | 248 | 248 | 250 | 240 | 240 | 240 | 1.5 | 3.5 | 4.5 | 0.3 | 0.7 | 1 | 0 | 0.1 | 0.1 | 0.3 | 0.6 | 1 | 5 | 11 | 16 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.8 | 12.9 | 13.2 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 80 | 50 | 60 | ♡ |  | 7223 |  | 7111 | KLMFEP-33001
4000647410 | SC_PM_QTR_UPS_4000647410.pdf | RAN | 20/10/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 34.1 | 40.3 | 234 | 50.03 | 50 | 266 | 266 | 0 | 0 | 0 | 245 | 244 | 245 | 244 | 243 | 246 | 239 | 239 | 240 | 2.2 | 4 | 5.2 | 0.5 | 0.9 | 1.2 | 0 | 0.1 | 0.1 | 0.5 | 0.8 | 1.2 | 8 | 13 | 19 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Breaker 2 and 3 not function, waiting for new battery |  | 11727 |  | 7256 | KLMFEP-33001
4000576174 | SC_PM_QTR_UPS_4000576174.pdf | RAN | 20/10/2023 |  | TRUE | TRUE | TRUE | TRUE |  | 100 |  |  | 236 | 50.02 | 50 | 266 | 266 | 0 | 0 | 0 | 242 | 241 | 244 | 243 | 241 | 244 | 240 | 240 | 240 | 1.9 | 3.7 | 4.9 | 0.4 | 0.8 | 1.2 | 0 | 0.2 | 0.1 | 0.4 | 0.8 | 1.1 | 6 | 13 | 18 | TRUE | TRUE | TRUE | [33 empty] | All equipment in good condition |  | 20160 |  | 7111 | KLMFEP-33001
4000493784 | SC_PM_QTR_UPS_4000493784.pdf | RAN | 20/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 32.7 | 39.0 | 228 |  |  | 266 | 266 | 0 | 0.1 | 0 | 242 | 241 | 242 | 241 | 240 | 241 | 239 | 239 | 240 | 2.1 | 3.8 | 5.3 | 0.5 | 0.8 | 1.2 | 0 | 0.1 | 0.2 | 0.5 | 0.8 | 1.2 | 7 | 12 | 19 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.3 | 13.4 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 90 | Good Condition. |  | 7223 |  | 7111 | KLMFEP-33001
4000480709 | SC_PM_QTR_UPS_4000480709.pdf | RAN | 2022-07-20 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 34.5 | 40.6 | 217 |  |  | 266 | 266 | 0 | 0.1 | 0 | 242 | 241 | 244 | 241 | 240 | 243 | 240 | 131 | 7 | 2.2 | 3.4 | 5.5 | 0.5 | 0.8 | 1.2 | 0 | 0.1 | 0.1 | 0.5 | 0.9 | 1.1 | 8 | 12 | 18 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.4 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 100 | 90 | 50 | 90 | all equitment in good conditions | ABDUL AZIN | 11727 | AZHAR YUNUS | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_11.pdf | RAN | 20/07/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 37.7 | 43.7 | 220 |  |  | 266 | 266 | 0 | 0 | 0 | 243 | 243 | 245 | 244 | 243 | 246 | 240 | 240 | 240 | 2.2 | 3.9 | 5.5 | 0.5 | 0.9 | 1.2 | 0 | 0.2 | 0.1 | 0.5 | 0.9 | 1.3 | 7 | 15 | 19 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Battery in good condition and all cable at bank properly connected |  | 20160 |  | 7223 | KLMFEP-33001
4000555093 | SC_PM_QTR_UPS_4000555093.pdf | RAN | 20/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.8 | 39.0 | 229 | 50 | 50 | 267 | 267 | 0 | 0.1 | 0 | 242 | 241 | 242 | 241 | 240 | 242 | 239 | 239 | 240 | 2.1 | 3.8 | 5.3 | 0.5 | 0.8 | 1.2 | 0 | 0.1 | 0.1 | 0.5 | 0.8 | 1.3 | 7 | 12 | 19 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [7 empty] | 7222 |  | 7111 | KLMFEP-33001
4000608067 | SC_PM_QTR_UPS_4000608067.pdf | RAN | 20/04/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36.8 | 41.5 | 230 | 50.04 | 50 | 266 | 266 | 0 | 0 | 0 | 242 | 242 | 244 | 243 | 241 | 244 | 240 | 240 | 240 | 1.8 | 3.8 | 5.3 | 0.4 | 0.8 | 1.3 | 0 | 0.2 | 0.1 | 0.4 | 0.9 | 1.2 | 6 | 14 | 19 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Module and battenes in good condition. Bank 2 and 3 don't have batteries Only used Bank 1. |  | 19921 |  | 7111 | KLMFEP-33001
4000530706 | SC_PM_QTR_UPS_4000530706.pdf | RAN | 20/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.4 | 34.6 | 246 | 50 | 50 | 268 | 268 | 0 | 0 | 0 | 234 | 234 | 240 | 236 | 238 | 236 | 240 | 240 | 240 | 1.6 | 4.5 | 3.7 | 0.4 | 1 | 0.8 | 0 | 0.2 | 0.1 | 0.3 | 1.1 | 0.8 | 5 | 15 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.2 | 12.8 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 200 | 100 | 100 | 50 | 100 | all equipment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
4000467101 | SC_PM_QTR_UPS_4000467101.pdf | RAN | 20/04/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 49.5 | 32.5 | 150 | 50 | 50 | 298 | 282 | 0 | 0 | 0 | 246 | 247 | 249 | 282 | 281 | 283 | 244 | 242 | 241 | 0.1 | 0.1 | 0.2 | 1 | 1.1 | 1.2 | 0.1 | 0.2 | 0.5 | 0.4 | 0.7 | 0.6 | 8 | 16 | 23 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.8 | 15.2 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 120 | 100 | 80 | 50 | 80 | ok |  | 7110 |  | 7111 | KLMFEP-33001
4000668095 | SC_PM_QTR_UPS_4000668095.pdf | RAN | 20/01/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36.8 | 43.0 | 237 |  |  | 266 | 266 | 0 | 0 | 0 | 241 | 240 | 243 | 241 | 240 | 243 | 240 | 240 | 240 | 2 | 4.1 | 4.9 | 0.5 | 0.9 | 1.2 | 0 | 0.3 | 0.1 | 0.5 | 1 | 1.2 | 7 | 13 | 17 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Only one bank (Bank A and Bank B) Other that, all equipment in a good conditions. |  | 22777 |  | 7222 | KLMFEP-33001
4000597864 | SC_PM_QTR_UPS_4000597864.pdf | RAN | 20/01/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.1 | 37.1 | 230 | 50.08 | 50 | 266 | 266 | 0 | 0 | 0 | 243 | 242 | 245 | 242 | 242 | 245 | 240 | 239 | 240 | 2 | 3.7 | 5.3 | 0.4 | 0.9 | 1.2 | 0 | 0.1 | 0.1 | 0.5 | 1 | 1.2 | 7 | 13 | 18 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | - Battery Bank 3 (EO1 - F40) need to be replaced - Battery 3 value is below 12V (EO1 - F40) |  | 20079 |  | 7111 | KLMFEP-33001
4000509057 | SC_PM_QTR_UPS_4000509057.pdf | RAN | 20/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 32.7 | 39.0 | 208.8 | 50 | 50 | 266 | 266 | 0 | 0.1 | 0.1 | 242 | 241 | 242 | 241 | 240 | 242 | 239 | 239 | 240 | 211 | 3.8 | 5.3 | 0.5 | 0.8 | 1.2 | 0 | 0.1 | 0.2 | 0.5 | 0.8 | 1.2 | 7 | 12 | 19 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.1 | 12.9 | 12.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 90 |  |  | 7222 |  | 7111 | KLMFEP-33001
4000446322 | SC_PM_QTR_UPS_4000446322.pdf | RAN | 20/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 48.5 | 32.5 | 150 | 50 | 50 | 282 | 253 | 0 | 0 | 0 | 246 | 247 | 249 | 282 | 281 | 283 | 244 | 242 | 241 | 0.1 | 0.1 | 0.2 | 1 | 1.1 | 1.2 | 0.1 | 0.2 | 0.5 | 0.4 | 0.7 | 0.6 | 8 | 1.6 | 2.3 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.8 | 13.2 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 100 | 50 | 50 | 80 | ok |  | 7223 |  | 7111 | KLMFEP-33001
4000646740 | SC_PM_QTR_UPS_4000646740.pdf | BNG | 19/10/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.3 | 34.2 | 268.8 | 50.02 | 50 | 266 | 266 | 0 | 0 | 0 | 245 | 243 | 246 | 245 | 245 | 246 | 240 | 239 | 240 | 2.7 | 6.1 | 3.9 | 0.6 | 1.4 | 0.9 | 0.1 | 0 | 0 | 0.6 | 1.5 | 0.8 | 10 | 22 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipments in a good condition. |  | 22547 |  | 7262 | KLMFEP-33001
4000576113 | SC_PM_QTR_UPS_4000576113.pdf | BNG | 19/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 40.3 | 43.7 | 50 | 50 | 50 | 266 | 266 | 0 | 0 | 0 | 252 | 249 | 252 | 251 | 250 | 253 | 240 | 239 | 240 | 3 | 6.4 | 3.7 | 0.7 | 1.4 | 0.8 | 0.1 | 0.2 | 0.1 | 0.7 | 1.4 | 0.9 | 10 | 23 | 13 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.4 | 13.2 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 50 | 100 | 49 | 48 | 49 | All in good condition |  | 19898 |  | 7111 | KLMFEP-33001
4000493756 | SC_PM_QTR_UPS_4000493756.pdf | BNG | 19/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.2 | 36.4 | 228 |  |  | 260 | 266 | 0 | 0 | 0 | 230 | 249 | 253 | 249 | 249 | 254 | 239 | 239 | 240 | 2.7 | 3.1 | 3.8 | 0.6 | 1.4 | 0.9 | 0 | 0.2 | 0 | 5.6 | 1.4 | 1.8 | 9 | 22 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.6 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 150 | 100 | 70 | 50 | 70 | Good Condition. |  | 7223 |  | 7111 | KLMFEP-33001
4000480668 | SC_PM_QTR_UPS_4000480668.pdf | BNG | 2022-07-19 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 32.4 | 36.4 | 48 | 50 | 50 | 260 | 264 | 0 | 0 | 0 | 250 | 249 | 253 | 249 | 244 | 253 | 239 | 239 | 240 | 2.7 | 3.1 | 3.8 | 0.6 | 1.4 | 0.9 | 0 | 0.2 | 0 | 0.6 | 1.4 | 1.8 | 9 | 22 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.1 | 13.6 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 150 | 100 | 70 | 50 | 70 | all equitment in good condition | ABDUL AZIN | 11727 | AZHAR YUNUS | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_8.pdf | BNG | 19/07/2024 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 31.6 | 33.1 | 591 |  |  | 266 | 266 | 0 | 0 | 0 | 245 | 244 | 247 | [6 empty] | 2.7 | 6.4 | 3.4 | 0.6 | 1.5 | 0.8 | 0.1 | 0 | 0 | 0.6 | 1.5 | 1.9 | 10 | 23 | 13 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | all ementien in good condition |  | 20159 |  | 7256 | KLMFEP-33001
4000555042 | SC_PM_QTR_UPS_4000555042.pdf | BNG | 19/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 46.0 | 50.9 | 54 | 50 | 50 | 266 | 264 | 0 | 0 | 0 | 246 | 243 | 246 | 245 | 239 | 240 | 240 | 239 | 240 | 2.7 | 5.5 | 3.5 | 0.6 | 1.2 | 0.6 | 0.1 | 0.2 | 0.1 | 0.6 | 1.2 | 0.8 | 12 |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | An equipment in good conditions |  | 7256 |  | 7111 | KLMFEP-33001
4000608017 | SC_PM_QTR_UPS_4000608017.pdf | BNG | 19/04/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.4 | 36.5 | 616.2 | 50 | 50 | 266 | 267 | 0 | 0 | 0 | 243 | 242 | 245 | 244 | 242 | 246 | 240 | 240 | 239 | 2.7 | 6.5 | 3.9 | 0.6 | 0.5 | 0.7 | 0 | 0.1 | 0 | 0.6 | 0.4 | 1.7 | 9 | 22 | 12 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | ADC change 2 module UPS. Bank 3 dosnt have batteries. Module and all batteries in good condition. |  | 19921 |  | 7111 | KLMFEP-33001
4000530667 | SC_PM_QTR_UPS_4000530667.pdf | BNG | 19/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 46.0 | 50.9 | 54 |  |  | 266 | 266 | 0 | 0 | 0 | 246 | 243 | 246 | 245 | 243 | 247 | 240 | 239 | 240 | 2.7 | 5.5 | 3.5 | 0.6 | 1.2 | 0.7 | 0.1 | 0.2 | 0.1 | 0.6 | 1.2 | 0.8 | 10 | 101 | 12 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.4 | 12.8 | 13.9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 55 | 100 | 25 | 50 | 55 | all equipment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
4000467069 | SC_PM_QTR_UPS_4000467069.pdf | BNG | 19/04/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 220 | 50 | 50 | 270 | 270 | 0 | 0 | 0 | 249 | 246 | 249 | 248 | 247 | 230 | 239 | 239 | 240 | 2.7 | 4.8 | 3.9 | 0.6 | 0.6 | 1 | 0 | 0.1 | 0 | 0.6 | 1.1 | 1 | 10 | 16 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.7 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 100 | 50 | 50 | 90 | 2 battery bank faulty |  | 7110 |  | 7111 | KLMFEP-33001
4000660374 | SC_PM_QTR_UPS_4000660374.pdf | BNG | 19/01/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.2 | 31.9 | 606 | 50 | 50 | 266 | 266 | 0 | 0 | 0 | 249 | 247 | 251 | 249 | 247 | 251 | 240 | 239 | 240 | 2.8 | 6.2 | 3.6 | 0.6 | 1.4 | 1 | 0.2 | 0.1 | 0.1 | 0.6 | 1.4 | 0.8 | 10 | 22 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipment in a good condition. |  | 22775 |  | 7110 | KLMFEP-33001
4000597708 | SC_PM_QTR_UPS_4000597708.pdf | BNG | 19/01/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 32.8 | 35.7 | 53 |  |  | 266 | 266 | 0 | 0 | 0 | 248 | 246 | 250 | 247 | 246 | 250 | 239 | 239 | 240 | 3 | 6.6 | 4 | 0.7 | 1.6 | 0.9 | 0 | 0.2 | 0 | 0.7 | 1.6 | 1 | 11 | 24 | 15 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Module need to calibrate. All battery in good condition. |  | 20452 |  | 7111 | KLMFEP-33001
4000509121 | SC_PM_QTR_UPS_4000509121.pdf | BNG | 19/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.1 | 36.4 | 220 | 50 | 50 | 260 | 266 | 0 | 0 | 0 | 230 | 249 | 253 | 249 | 249 | 254 | 239 | 239 | 240 | 2.7 | 3.1 | 3.8 | 0.6 | 1.4 | 0.9 | 0 | 0.2 | 0 | 0.6 | 1.4 | 1.8 | 9 | 22 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.4 | 13.2 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 150 | 100 | 75 | 50 | 75 |  |  | 7222 |  | 7111 | KLMFEP-33001
4000446363 | SC_PM_QTR_UPS_4000446363.pdf | BNG | 19/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 45.8 | 50.7 | 220 |  |  | 270 | 270 | 0 | 0 | 0 | 249 | 296 | 249 | 248 | 247 | 280 | 239 | 239 | 240 | 2.7 | 4.8 | 3.9 | 0.6 | 0.6 | 1 | 0 | 0.1 | 0 | 0.6 | 1.1 | 1 | 10 | 16 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.7 | 12.8 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 80 | 100 | 40 | 50 | 40 | 2 battery book faulty |  | 7222 |  | 7111 | KLMFEP-33001
4000644023 | SC_PM_QTR_UPS_4000644023.pdf | IBI | 18/10/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36.0 | 42.7 | 123 |  |  | 266 | 266 | 0 | 0 | 0 | 245 | 245 | 248 | 245 | 245 | 247 | 239 | 239 | 239 | 2.9 | 7.1 | 10.4 | 0.6 | 1.4 | 2.4 | 0 | 0.5 | 0.5 | 0.6 | 1.6 | 2.5 | 10 | 25 | 38 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipments in a good condition. |  | 22547 |  | 7262 | KLMFEP-33001
4000576144 | SC_PM_QTR_UPS_4000576144.pdf | IBI | 18/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 30 | 35.4 | 120 | 50.02 | 50 | 233 | 273 | 0 | 0 | 0 | 252 | 252 | 256 | 252 | 252 | 254 | 239 | 239 | 239 | 2.9 | 6.7 | 11.3 | 0.7 | 1.3 | 2.6 | 0 | 0.5 | 0.5 | 0.6 | 1.7 | 2.7 | 22 | 32 | 40 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.3 | 13.4 | [25 empty] | Slave module faulty only use 1 bank batteries |  | 19898 |  | 7111 | KLMFEP-33001
4000493774 | SC_PM_QTR_UPS_4000493774.pdf | IBI | 18/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36 |  | 138 | 50 | 50 | 236 | 236 | 0 | 0 | 0 | 250 | 250 | 251 | 250 | 250 | 252 | 239 | 239 | 240 | 3.2 | 6.9 | 7.7 | 0.7 | 1.5 | 2 | 0.1 | 0.4 | 0.2 | 0.7 | 1.6 | 1.9 | 11 | 23 | 29 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.8 | 12.9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 186 | 100 | 80 | 50 |  |  |  | 7222 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_5.pdf | IBI | 18/07/2024 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 40.7 | 48.1 | 111 |  |  | 266 | 266 | 0 | 0 | 0 | 242 | 242 | 245 | 242 | 242 | 244 |  |  |  | 2.9 | 7 | 10.7 | 0.6 | 1.4 | 2.6 | 0 | 0.5 | 0.5 | 0.6 | 1.7 | 2.6 | 10 | 27 | 39 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | UPS in good condition. |  | 20159 |  | 7256 | KLMFEP-33001
4000555072 | SC_PM_QTR_UPS_4000555072.pdf | IBI | 18/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 46.0 | 50.9 | 54 |  |  | 266 | 266 | 0 | 0 | 0 | 246 | 243 | 246 | 245 | 243 | 247 | 240 | 239 | 240 | 2.7 | 5.5 | 3.5 | 0.6 | 1.2 | 0.7 | 0.1 | 0.2 | 0.1 | 0.6 | 1.2 | 0.8 | 10 | 19 | 12 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | all equipment in good condition. |  | 7256 |  | 7111 | KLMFEP-33001
4000480689 | SC_PM_QTR_UPS_4000480689.pdf | IBI | 18/07/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36 |  | 129 | 50 | 50 | 286 | 286 | 0 | 0 | 0 | 250 | 250 | 254 | 250 | 250 | 252 | 239 | 239 | 240 | 3.2 | 6.9 | 7.7 | 0.7 | 1.5 | 2 | 0 | 0.4 | 0.2 | 0.7 | 1.6 | 1.9 | 11 | 23 | 29 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.8 | 12.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 190 | 100 | 80 | 50 | 80 | ok | ROHIZAN | 7223 | AZHAR YUNUS | 7111 | KLMFEP-33001
4000608042 | SC_PM_QTR_UPS_4000608042.pdf | IBI | 18/04/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 120 | 50.04 | 50 | 269 | 269 | 0 | 0 | 0 | 251 | 251 | 255 | 251 | 251 | 252 | 240 | 239 | 239 | 2.9 | 6.5 | 10.8 | 0.7 | 1.4 | 2.6 | 0 | 0.5 | 0.4 | 0.7 | 1.6 | 2.5 | 11 | 23 | 38 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Equipment is in good condition. Battery bank 2 no batery (C and D) |  | 20449 |  | 7111 | KLMFEP-33001
4000530683 | SC_PM_QTR_UPS_4000530683.pdf | IBI | 18/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 37.7 | 44.7 | 122 |  |  | 268 | 268 | 0 | 0 | 0 | 252 | 253 | 256 | 253 | 253 | 254 | 239 | 239 | 239 | 2.7 | 6.2 | 11.4 | 0.6 | 1.4 | 2.6 | 0 | 0.5 | 0.5 | 0.6 | 1.4 | 2.7 | 9 | 22 | 41 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.2 | 12.8 | 13 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 150 | 100 | 100 | 50 | 180 | all equitment in good conditions #1 unit bateri bank not good condition 1 unit module faulty |  | 11727 |  | 7111 | KLMFEP-33001
4000467087 | SC_PM_QTR_UPS_4000467087.pdf | IBI | 18/04/2022 |  | TRUE | TRUE | 1 unit module faults (share module) | TRUE | TRUE | 100 | 36.4 | 44.4 | 137 |  |  | 206 | 286 | 0 | 0 | 0 | 250 | 250 | 254 | 250 | 250 | 254 | 239 | 259 | 239 | 3.2 | 6.9 | 7.4 | 0.7 | 1.5 | 2 | 0 | 0.4 | 0.2 | 0.7 | 1.6 | 1.9 | 11 | 23 | 29 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.4 | 12.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 150 | 100 | 80 | 50 | 150 | OK |  | 7110 |  | 7111 | KLMFEP-33001
4000669108 | SC_PM_QTR_UPS_4000669108.pdf | IBI | 18/01/2025 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 31.5 | 35.2 | 121.8 |  |  | 266 | 266 | 0 | 0 | 0 | 243 | 243 | 246 | 243 | 243 | 245 | 240 | 240 | 239 | 2.9 | 6.8 | 4.7 | 0.6 | 1.5 | 2.5 | 0 | 0.6 | 0.5 | 0.7 | 1.7 | 2.5 | 10 | 25 | 36 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipment in a good condition |  | 22775 |  | 7110 | KLMFEP-33001
4000597779 | SC_PM_QTR_UPS_4000597779.pdf | IBI | 18/01/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.5 | 38.1 | 120 |  |  | 268 | 268 | 0 | 0 | 0 | 245 | 246 | 249 | 245 | 246 | 248 | 239 | 239 | 240 | 3.2 | 6.5 | 10.7 | 0.7 | 1.4 | 2.5 | 0 | 0.5 | 0.5 | 0.7 | 1.6 | 2.5 | 11 | 23 | 38 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | -Module P2 notified alarm Phase Fault -there are serval Faulty battery burn -beside that hardware in good condition - Bank 1 and 2 kembung |  | 20079 |  | 7111 | KLMFEP-33001
4000509107 | SC_PM_QTR_UPS_4000509107.pdf | IBI | 18/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36 |  | 190 | 60 | 50 | 286 | 286 | 0 | 0 | 0 | 250 | 250 | 254 | 250 | 250 | 254 | 239 | 239 | 240 | 3.2 | 6.4 | 7.1 | 0.4 | 1.5 | 2 | 0 | 0.4 | 0.2 | 0.7 | 1.6 | 1.9 | 11 | 24 | 30 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.8 | 12.9 | 12.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 140 | 100 | 95 | 50 | 95 | All equipment in good condition. | YARUL AZWAN | 7110 |  |  | KLMFEP-33001
4000446346 | SC_PM_QTR_UPS_4000446346.pdf | IBI | 18/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36.4 | 44.4 | 137 |  |  | 286 | 286 | 0 | 0 | 0 | 280 | 250 | 254 | 280 | 250 | 254 | 239 | 239 | 239 | 3.2 | 6.9 | 7.7 | 0.7 | 1.5 | 2 | 0 | 0.4 | 0.2 | 0.7 | 1.6 | 1.9 | 11 | 23 | 29 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.8 | 12.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 160 | 100 | 80 | 50 | 80 | ok |  | 7222 |  | 7111 | KLMFEP-33001
4000576134 | SC_PM_QTR_UPS_4000576134.pdf | HAH | 17/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.3 | 38.8 | 233 | 50.5 | 50 | 267 | 267 | 0.1 | 0.1 | 0 | 238 | 238 | 240 | 236 | 237 | 240 | 239 | 239 | 246 | 1.5 | 6.3 | 3.4 | 0.4 | 1.4 | 0.7 | 1 | 0.1 | 0.1 | 0.4 | 1.4 | 0.7 | 6 | 22 | 10 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | all equipment in good conditiong |  | 7256 |  | 7111 | KLMFEP-33001
4000493769 | SC_PM_QTR_UPS_4000493769.pdf | HAH | 17/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36 |  | 372 | 50 | 50 | 271 | 271 | 0 | 0 | 0 | 237 | 236 | 239 | 238 | 236 | 239 | 239 | 239 | 240 | 1.4 | 2.3 | 2.7 | 0.3 | 0.5 | 0.6 | 0 | 0 | 0.1 | 0.3 | 0.5 | 0.6 | 5 | 8 | 9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.5 | 12.6 | 12.5 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 90 |  |  | 7222 |  | 7111 | KLMFEP-33001
4000646788 | SC_PM_QTR_UPS_4000646788.pdf | HAH | 17/10/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 321 |  |  | 267 | 267 | 0 | 0 | 0 | 240 | 239 | 242 | 239 | 238 | 242 | 239 | 240 | 240 | 1.5 | 3.6 | 2.9 | 0.3 | 0.8 | 0.6 | 10 | 0 | 0.1 | 0.3 | 0.8 | 0.6 | 5 | 12 | 9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipment in a good condition. |  | 20858 |  | 7262 | KLMFEP-33001
| SC_PM_NA_UPS_NA_6.pdf | HAH | 17/07/7024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 37.1 | 42.9 | 315 |  |  | 267 | 267 | 0 | 0.1 | 0 | 241 | 239 | 242 | 241 | 239 | 241 |  |  |  | 1.6 | 3.5 | 3.4 | 0.4 | 0.8 | 0.7 | 0 | 0 | 0 | 0.3 | 0.8 | 0.7 | 5 | 13 | 10 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipment in good condition. |  | 19920 |  | 7256 | KLMFEP-33001
4000555066 | SC_PM_QTR_UPS_4000555066.pdf | HAH | 17/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.9 | 39.9 | 280 |  |  | 267 | 267 | 0.1 | 0.1 | 0 | 237 | 236 | 239 | 238 | 236 | 239 | 239 | 239 | 240 | 1.6 | 3.6 | 2.8 | 0.3 | 0.7 | 0.8 | 0 | 0 | 0 | 0.3 | 0.8 | 0.8 | 5 | 13 | 12 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | all equipment in good condition |  | 7256 |  | 7111 | KLMFEP-33001
4000480684 | SC_PM_QTR_UPS_4000480684.pdf | HAH | 17/07/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36 |  | 380 |  |  | 271 | 271 | 0 | 0 | 0 | 237 | 236 | 239 | 237 | 236 | 239 | 238 | 239 | 239 | 1.4 | 2.3 | 2.7 | 0.3 | 0.5 | 0.6 | 0 | 0 | 0.1 | 0.3 | 0.5 | 0.6 | 8 | 8 | 9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.5 | 12.6 | 12.8 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 170 | 100 | 90 | 50 | 90 |  | ROHIZAN | 7223 | AZHAR YUNUS | 7111 | KLMFEP-33001
4000608037 | SC_PM_QTR_UPS_4000608037.pdf | HAH | 17/04/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 254 | 50.5 | 50 | 267 | 267 | 0.1 | 0.1 | 0 | 239 | 237 | 240 | 238 | 237 | 240 | 239 | 239 | 240 | 1.6 | 3.5 | 3.7 | 0.4 | 0.8 | 0.7 | 0 | 0 | 0 | 0.3 | 0.9 | 0.7 | 5 | 12 | 11 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Bank 1 & Bank 2 dismantle further maintenance |  | 20449 |  | 7111 | KLMFEP-33001
4000530679 | SC_PM_QTR_UPS_4000530679.pdf | HAH | 17/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36.9 | 43.0 | 240 |  |  | 267 | 267 | 0 | 0.1 | 0 | 239 | 237 | 239 | 238 | 237 | 240 | 239 | 240 | 240 | 1.6 | 6.1 | 2.6 | 0.4 | 1.3 | 0.7 | 0 | 0 | 0.1 | 0.4 | 1.4 | 0.6 | 5 | 21 | 9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.8 | 13.2 | 13.1 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 150 | 100 | 150 | 50 | 180 | all equipment |  | 11727 |  | 7111 | KLMFEP-33001
4000467082 | SC_PM_QTR_UPS_4000467082.pdf | HAH | 17/04/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 37.9 | 58.9 | 326 | 50.06 | 50 | 271 | 271 | 0 | 0 | 0 | 238 | 237 | 240 | 238 | 237 | 24 | 239 | 239 | 240 | 1.3 | 3.8 | 2.6 | 0.3 | 0.8 | 0.6 | 0 | 0 | 0.1 | 0.3 | 0.9 | 0.6 | 4 | 15 | 9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.4 | 13.4 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 150 | 100 | 80 | 50 | 80 | all equitment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
4000669114 | SC_PM_QTR_UPS_4000669114.pdf | HAH | 17/01/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 30.8 | 34.7 | 273 |  |  | 26.7 | 26.7 | 0 | 0 | 0 | 235 | 234 | 236 | 235 | 234 | 239 | 239 | 240 | 240 | 1.4 | 3.8 | 2.6 | 0.3 | 0.8 | 0.6 | 0 | 0.1 | 0.1 | 0.3 | 0.9 | 0.6 | 5 | 13 | 10 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All battery and module working properly without any error. Bank 1 and 2 not available. Only bank 3 is available and in good condition |  | 22775 |  | 7110 | KLMFEP-33001
4000597748 | SC_PM_QTR_UPS_4000597748.pdf | HAH | 17/01/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 35.7 | 41.5 | 330 | 50.04 | 50 | 267 | 267 | 0.1 | 0.1 | 0 | 240 | 237 | 240 | 238 | 237 | 240 | 240 | 239 | 240 | 1.5 | 3.5 | 3 | 0.3 | 0.8 | 0.7 | 0 | 0 | 0 | 0.3 | 0.8 | 0.7 | 5 | 13 | 10 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | * all battery fault except bank F. * condition both module in good condition. * battery take out. except bank F |  | 19898 |  | 7111 | KLMFEP-33001
4000509110 | SC_PM_QTR_UPS_4000509110.pdf | HAH | 17/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 24 |  | 126 | 50 | 50 | 277 | 271 | 0 | 0 | 0 | 255 | 254 | 256 | 255 | 254 | 256 | 239 | 239 | 239 | 3.2 | 6.3 | 7.6 | 0.7 | 1.5 | 1.8 | 0 | 0.3 | 0.5 | 0.7 | 1.6 | 1.8 | 11 | 19 | 20 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.5 | 12.6 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 160 | 100 | 80 | 50 | 60 | All annection cable with battery in secure procution. |  | 1110 |  | 7111 | KLMFEP-33001
4000446351 | SC_PM_QTR_UPS_4000446351.pdf | HAH | 17/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36.6 | 49.4 | 332 |  | 50 | 271 | 271 | 0 | 0 | 0 | 247 | 247 | 239 | 248 | 276 | 239 | 239 | 239 | 239 | 1.11 | 2.3 | 2.7 | 0.3 | 0.5 | 0.6 | 0 | 0 | 0.1 | 0.3 | 0.5 | 0.6 | 5 | 8 | 9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.6 | 12.8 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 160 | 100 | 80 | 50 | 150 | All equipment in good condition |  | 7222 |  | 7111 | KLMFEP-33001
4000576156 | SC_PM_QTR_UPS_4000576156.pdf | MAH | 16/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 34.7 | 41.6 | 122 |  |  | 267 | 267 | 0 | 0 | 0 | 243 | 242 | 243 | 243 | 243 | 244 | 239 | 239 | 239 | 3.4 | 6.2 | 10.4 | 0.7 | 1.3 | 2.2 | 0 | 0.3 | 0.7 | 0.8 | 1.7 | 2.5 | 11 | 23 | 37 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All good condition |  | 19920 |  | 7111 | KLMFEP-33001
4000493791 | SC_PM_QTR_UPS_4000493791.pdf | MAH | 16/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 34 |  | 136 | 50 | 50 | 271 | 271 | 0 | 0.7 | 0 | 255 | 254 | 253 | 255 | 256 | 256 | 239 | 239 | 239 | 3.2 | 6.3 | 7.6 | 0.7 | 1.5 | 1.8 | 0 | 0.3 | 0.5 | 0.7 | 1.5 | 0.8 | 11 | 23 | 27 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.5 | 12.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 160 | 100 | 80 | 50 | 60 |  |  | 7222 |  | 7111 | KLMFEP-33001
4000646818 | SC_PM_QTR_UPS_4000646818.pdf | MAH | 16/10/2024 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 36 | 40.9 | 128 | 50 | 50 | 267 | 267 | 0 | 0 | 0 | 243 | 241 | 246 | 243 | 242 | 245 | 239 | 239 | 239 | 3.6 | 7.6 | 9.6 | 0.8 | 1.6 | 2.2 | 0.1 | 0.4 | 0.6 | 0.4 | 1.6 | 2.2 | 12 | 23 | 34 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipment in good condition |  | 22547 |  | 7202 | KLMFEP-33001
| SC_PM_NA_UPS_NA_13.pdf | MAH | 16/07/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 35.2 | 42 | 126 | 50.04 | 50 | 267 | 267 | 0 | 0.1 | 0 | 248 | 247 | 249 | 248 | 248 | 250 | 239 | 239 | 239 | 36 | 6 | 9 | 0.8 | 1.5 | 2 | 0.1 | 0.3 | 0.5 | 0.4 | 1.5 | 2.2 | 13 | 23 | 34 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipment in good condition |  | 9920 |  | 7256 | KLMFEP-33001
4000541165 | SC_PM_QTR_UPS_4000541165.pdf | MAH | 16/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 65 |  | 100 | 50 | 80 | 267 | 207 | 0 | 0.1 | 0 | 245 | 245 | 247 | 246 | 246 | 246 | 239 | 239 | 241 | 5.2 | 5.6 | 10.4 | 0.8 | 1.4 | 2.3 | 0 | 0.3 | 0.6 | 0.8 | 1.4 | 2.4 | 12 | 25 | 38 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | one module operated |  | 7223 |  | 7111 | KLMFEP-33001
4000480697 | SC_PM_QTR_UPS_4000480697.pdf | MAH | 16/07/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 30 |  | 129.6 | 50 | 50 | 271 | 271 | 0 | 0.7 | 0 | 255 | 254 | 256 | 255 | 256 | 256 | 239 | 237 | 239 | 3.2 | 6.3 | 7.6 | 0.7 | 15 | 1.8 | 0 | 0.3 | 0.5 | 0.7 | 1.5 | 0.8 | 11 | 23 | 27 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.8 | 12.6 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 160 | 100 | 80 | 50 | 60 | OK | ROHIZAN | 7223 | AZHAR YUNUS | 7111 | KLMFEP-33001
4000608051 | SC_PM_QTR_UPS_4000608051.pdf | MAH | 16/04/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 133 | 50 | 50 | 267 | 267 | 0.1 | 0.1 | 0 | 247 | 246 | 248 | 248 | 248 | 249 | 239 | 239 | 239 | 2.7 | 7.1 | 9.6 | 0.9 | 1.5 | 2.2 | 0 | 0.3 | 0.6 | 0.6 | 1.5 | 2.3 | 9 | 22 | 35 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Bank 1 TRANSFER to HanG TUAH. Module 1 Problem.Equipment in good condition |  | 20449 |  | 7011 | KLMFEP-33001
4000530695 | SC_PM_QTR_UPS_4000530695.pdf | MAH | 16/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 35.8 |  | 120 | 50 | 50 | 267 | 267 | 0 | 0 | 0 | 245 | 244 | 246 | 245 | 245 | 245 | 239 | 240 | 239 | 2.7 | 6.7 | 9.6 | 0.6 | 1.5 | 2.2 | 0 | 0.3 | 0.5 | 0.6 | 1.6 | 2.3 | 10 | 23 | 37 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.3 | 12.2 | 12.5 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 120 | 100 | 60 | 50 | 60 |  |  | 7223 |  | 7111 | KLMFEP-33001
4000467093 | SC_PM_QTR_UPS_4000467093.pdf | MAH | 16/04/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 32.2 | 38.9 | 133 | 50.01 | 50 | 271 | 271 | 0 | 0 | 0 | 248 | 248 | 248 | 248 | 249 | 249 | 239 | 239 | 240 | 2 |  | 6.9 | 0.4 | 1.4 | 2.4 | 0 | 0.2 | 0.8 | 0.5 | 1.4 | 2.6 | 7 | 23 | 37 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.6 | 13.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 60 | 50 | 60 | all equipment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
4000467110 | SC_PM_QTR_UPS_4000467110.pdf | TUN | 16/04/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 24.7 | 22.6 | 122 | 49.9 | 49.6 | 267 | 267 | 768.3 | 268.1 | 1.3 |  |  |  | 244 | 243 | 243 | 241 | 241 | 241 | 0.2 | 2.1 | 1.5 | 0.4 | 1.9 | 2.4 | 0 | 0.2 | 0.5 | 0.5 | 1.4 | 2.6 | 7 | 23 | 36 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.4 | 13.4 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 110 | 100 | 60 | 50 | 105 | all equipment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
4000668132 | SC_PM_QTR_UPS_4000668132.pdf | MAH | 16/01/2025 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 36.3 | 42.8 | 125 |  |  | 267 | 267 | 0 | 0.1 | 0 | 244 | 243 | 246 | 244 | 244 | 247 | 239 | 239 | 239 | 2.7 | 6.7 | 9.6 | 0.8 | 0.7 | 2.3 | 0.1 | 0.5 | 0.5 | 0.8 | 2.6 | 2.2 | 12 | 23 | 34 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Bank A not available, All battery in good condition. |  | 22775 |  | 7110 | KLMFEP-33001
4000597813 | SC_PM_QTR_UPS_4000597813.pdf | MAH | 16/01/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 39.0 | 45.8 | 122 | 50 | 50 | 267 | 267 | 0 | 0.1 | 0 | 246 | 246 | 247 | 247 | 247 | 248 | 239 | 239 | 239 | 3.3 | 6.3 | 9.5 | 0.8 | 1.6 | 2.3 | 0 | 0.2 | 0.6 | 0.8 | 1.5 | 2.3 | 12 | 22 | 35 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [11 empty] | 1. Only used 1 module because module power failure (module 1) 2. All batteries in good condition 3. Equipment in good condition. |  | 20826 |  | 7111 | KLMFEP-33001
4000509102 | SC_PM_QTR_UPS_4000509102.pdf | MAH | 16/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 30 |  | 136 | 50 | 50 | 271 | 271 | 0 | 0.7 |  | 255 | 254 | 236 | 255 | 256 | 256 | 239 | 239 | 239 | 2.2 | 6.3 | 7.6 | 0.7 | 1.5 | 1.3 | 0 | 0.3 | 0.5 | 0.7 | 1.5 | 1.8 | 11 | 23 | 27 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.4 | 13.2 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 160 | 100 | 80 | 80 | 60 | An eaupment modem and battery in good artition. |  | 7110 |  | 7111 | KLMFEP-33001
4000446338 | SC_PM_QTR_UPS_4000446338.pdf | MAH | 16/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 34.1 | 41.5 | 196 | 80 |  | 271 | 271 | 0 | 0 | 0 | 255 | 256 | 254 | 255 | 256 | 254 | 229 | 239 | 239 | 3.2 | 6.1 | 7.6 | 0.7 | 1.6 | 1.8 | 0 | 0.3 | 0.5 | 0.7 | 1.5 | 1.8 | 11 | 23 | 27 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.8 | 12.6 | 12.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 240 | 100 | 120 | 50 | 120 | ok |  | 7222 |  | 7111 | KLMFEP-33001
4000647425 | SC_PM_QTR_UPS_4000647425.pdf | Tun | 15/10/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 21 | 23 |  | 50 | 50 | 267 | 267 | 267 | 268 | 0 | 55 | 1 | 34 | 242 | 240 | 243 | 241 | 241 | 241 | 0.2 | 2.2 | 1.8 | 0.1 | 0.4 | 0.3 | 0.4 | 2 | 1.6 | 0.3 | 1 | 1 | 84.4 | 16.3 | 15.9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All in good condition |  | 19922 |  | 7248 | KLMFEP-33001
4000576195 | SC_PM_QTR_UPS_4000576195.pdf | Tun | 15/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  |  | 50 |  | 261 | 261 | 0 | 0 |  |  |  |  | 243 | 242 | 244 | 241 | 241 | 241 | 1 | 8.1 | 6.5 | 0.2 | 1.6 | 1.1 | 0.1 | 2 | 1.6 | 0 | 0.8 | 1 | 0.8 | 0.84 | 0.75 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.2 | 13.4 | 13.5 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 186 | 100 | 68 | 50 | 60 | good condition |  | 7248 |  | 7111 | KLMFEP-33001
4000509049 | SC_PM_QTR_UPS_4000509049.pdf | TUN | 15/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33 |  | 180 |  |  | 241 | 242 | 0.2 | 0.1 | 1.9 | 243 | 244 | 245 | 244 | 243 | 244 | 241 | 240 | 244 | 1.9 | 6.5 | 6.4 | 0.2 | 0.1 | 0.1 | 0.3 | 1.6 | 1.7 | 0.1 | 1.1 | 1.1 | 3.5 | 3.2 | 3 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.3 | 12.5 | 12.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 90 |  |  | 7222 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_4.pdf | TUN | 15/07/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 21.5 |  |  |  |  | 267.7 | 267.7 | 268.2 |  | 0 | 55 | 1 | 34 | 245.3 | 243.5 | 246.8 | 241.5 | 241.3 | 241.3 | 1.8 | 8 | 6.9 | 0.2 | 1.7 | 1.2 | 0.4 | 2 | 1.6 | 0.7 | 1 | 1 | 84.4 | 16.3 | 15.9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All in good condition |  | 20450 |  | 7262 | KLMFEP-33001
4000541175 | SC_PM_QTR_UPS_4000541175.pdf | TUN | 15/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  |  | 50 | 50 | 247 | 267 | 0 | 0 |  |  |  |  | 243 | 242 | 244 | 241 | 241 | 241 | 1.6 | 8.1 | 6.5 | 0.2 | 1.6 | 1.1 | 0.4 | 2 | 1.6 | 0 | 0.8 | 1.6 | 0.8 | 0.84 | 0.75 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | good condition. |  | 7223 |  | 7111 | KLMFEP-33001
4000480722 | SC_PM_QTR_UPS_4000480722.pdf | TUN | 15/07/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33 |  | 180 | 50 | 50 | 241 | 242 | 0.2 | 0.1 | 1.9 | 243 | 244 | 245 | 244 | 243 | 244 | 241 | 240 | 244 | 1.9 | 6.5 | 6.4 | 0.2 | 0.1 | 1.1 | 0.3 | 1.6 | 1.7 | 0.1 | 1.1 | 1.1 | 3.5 | 3.2 | 3 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.3 | 12.5 | 12 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 90 | ok | ROHIZAN | 7223 | AZHAR YUNUS | 7111 | KLMFEP-33001
4000608083 | SC_PM_QTR_UPS_4000608083.pdf | TUN | 15/04/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 30 |  | 70 | 50 | 50 | 267 | 267 | 0 | 0 | 0 | 55 | 1 | 34 | 244 | 244 | 246 | 241 | 241 | 241 | 1.9 | 8.3 | 6.5 | 0.2 | 1.7 | 1.2 | 0.4 | 2 | 1.6 | 0.3 | 1 | 1 | 8.4 | 16.3 | 15.9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | all equipment are in good condition |  | 20449 |  | 7111 | KLMFEP-33001
4000520523 | SC_PM_QTR_UPS_4000520523.pdf | TUN | 15/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 54 | 49.9 | 49.5 | 249 | 269 | [6 empty] | 240 | 239 | 241 | 241 | 241 | 247 | 1.9 | 8.2 | 6.4 | 0.1 | 0.5 | 0.5 |  |  |  | 0.5 | 0.5 | 0.4 |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.3 | 12.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 300 | 100 | 180 | 60 | 10 |  |  | 7223 |  | 7111 | KLMFEP-33001
4000668027 | SC_PM_QTR_UPS_4000668027.pdf | TUN | 15/01/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 30.2 | 31.3 | 230 |  |  | 267 | 268 | 0 | 0 | 0 | 244 | 243 | 246 | 244 | 244 | 247 | 239 | 239 | 239 | 2.7 | 6.2 | 9.6 | 0.8 | 0.7 | 2.3 | 0.1 | 0.7 | 2.3 | 0.8 | 2.6 | 2.2 | 12 | 23 | 34 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | all equiptment in good conditions |  | 11727 |  | 11727 | KLMFEP-33001
4000597877 | SC_PM_QTR_UPS_4000597877.pdf | TUN | 15/01/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 30 |  | 70 | 50 | 50 | 267 | 267 | 0 | 0 | 0 | 55 | 1 | 34 | 244 | 244 | 246 | 241 | 241 | 241 | 1.9 | 8.3 | 6.5 | 0.2 | 1.7 | 1.2 | 0.4 | 2 | 1.6 | 0.3 | 1 | 1 | 84.4 | 16.3 | 15.9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipment is in good condition |  | 19898 |  | 7111 | KLMFEP-33001
4000509048 | SC_PM_QTR_UPS_4000509048.pdf | TUN | 15/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 24 | 26 | 360 |  |  | 267.6 | 267.8 | 241.2 | 241.3 |  | 240 | 239 | 241 | 240 | 239 | 241 | 241 | 241 | 241 | 1.9 | 7.9 | 6.9 | 0.2 | 1.7 | 1.1 | 0.2 | 1.9 | 1.4 | 0.3 | 1 | 1 | 3.4 | 14.3 | 11.2 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.2 | 13.4 | 13.5 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 186 | 100 | 68 | 50 | 68 | All equipment module and battery in good condition. |  | 7110 |  | 7111 | KLMFEP-33001
4000446286 | SC_PM_QTR_UPS_4000446286.pdf | TUN | 15/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 34 |  | 180 | 50 | 50 | 241 | 242 | 0.2 | 0.1 | 1.9 | 243 | 241 | 245 | 243 | 244 | 244 | 241 | 240 | 244 | 1.9 | 6.5 | 4 | 0.2 | 0.1 | 1.1 | 0.3 | 1.6 | 1.7 | 0.1 | 1.1 | 1.1 | 3.5 | 3.2 | 3 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.2 | 12.5 | 12.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 90 | ok |  | 7110 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_1 (7).pdf | KLS | 14/10/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 35.2 | 43.6 | 224 | 50 | 50 | 267 | 268 | 0 | 0 | 0 | 256 | 255 | 257 | 255 | 255 | 256 | 239 | 238 | 239 | 2.3 | 3.8 | 5.3 | 0.5 | 0.9 | 1.2 | 0 | 0.2 | 0 | 0.5 | 0.9 | 1.2 | 8 | 13 | 19 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | -Bank A, B, C temporary take out by Adc |  | 19922 |  | 7248 | KLMFEP-33001
| SC_PM_NA_UPS_NA_1 (1).pdf | KLS | 14/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 34.8 | 41.6 | 210 |  |  | 267 | 268 | 0 | 0 | 0 | 255 | 254 | 256 | 254 | 254 | 255 | 239 | 240 | 240 | 2.5 | 5.9 | 6.3 | 0.6 | 0.8 | 1.4 | 10 | 0.2 | 0.2 | 0.5 | 0.9 | 1.5 | 8 | 13 | 22 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.7 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 100 | 60 | 80 | 120 | connection connector cable secure and system in good condition. |  | 7110 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA (9).pdf | KLS | 2025-01-14 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 214 | 50.05 | 50 | 267 | 268 | 0 | 0 | 0 | 255 | 253 | 256 | 254 | 256 | 255 | 239 | 238 | 239 | 2.3 | 4.7 | 5.8 | 0.5 | 0.9 | 1.3 | 0 | 0.2 | 0 | 0.5 | 1 | 1.3 | 8 | 16 | 20 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | The UPS only use one bank and one breaker. Everything is in good condition. This up's also use two module. |  | 22778 |  | 7110 | KLMFEP-33001
| SC_PM_NA_UPS_NA_10.pdf | KLS | 14/07/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 32.1 | 40.3 | 212 |  |  | 269 | 270 | 0 | 0 | 0 | 257 | 255 | 258 |  |  |  | 239 | 238 | 239 | 2.3 | 4.2 | 5.7 | 0.5 | 0.8 | 1.3 | 0 | 0.2 | 0.1 | 0.5 | 0.8 | 1.2 | 8 | 14 | 19 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All in good condition |  | 20450 |  | 7262 | KLMFEP-33001
| SC_PM_NA_UPS_NA (1).pdf | KLS | 14/07/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 40.1 |  | 49 | 14 | 50 | 20.7 | 24.8 | 0 | 0 | 0 | 248 | 248 | 247 | 249 | 248 | 248 | 230 | 230 | 231 | 5.3 | 5.3 | 10.3 | 1.2 | 1.2 | 2.3 | 0.3 | 0.1 | 0.4 | 1.2 | 1.2 | 2.3 | 19 | 10 | 25 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.7 | 12.05 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 100 | 60 | 50 | 120 |  |  | 7222 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA (5).pdf | KLS | 14/04/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 34.1 | 40.9 | 104 |  |  | 268 | 268 | 0 | 0 | 0 | 256 | 254 | 257 | 255 | 254 | 257 | 239 | 239 | 240 | 5 | 8.1 | 12.1 | 1.1 | 1.9 | 2.6 | 0.3 | 0.6 | 0.5 | 1.1 | 1.9 | 2.7 | 17 | 29 | 41 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipment in good Condition |  | 20449 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_1 (2).pdf | KLS | 14/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36.7 |  | 107 |  |  | 268 | 268 | 0 | 0 | 0 | 253 | 253 | 254 | 253 | 253 | 254 | 240 | 239 | 240 | 5 | 7.9 | 11.3 | 1.1 | 1.5 | 2.8 | 0.3 | 0.5 | 10.5 | 1.2 | 1.8 | 2.8 | 17 | 22 | 42 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.3 | 12.1 | 12.2 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 102 | 100 | 60 | 50 | 40 | 1 Module Foil/problem |  | 7223 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA.pdf | KLS | 14/04/2022 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 32.2 | 38.9 | 150 |  |  | 271 | 271 | 0 | 0 | 0 | 248 | 248 | 248 |  |  |  | 239 | 239 | 240 | 20 | 6.9 | 10.3 | 0.4 | 1.4 | 2.4 | 0 | 0.2 | 0.5 | 0.5 | 1.4 | 2 | 7 | 23 | 36 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.4 | 13.4 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  | 150 | 100 | 80 | 80 | 50 | all equitment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA (8).pdf | KLS | 14/01/2025 |  | TRUE | TRUE | TRUE | TRUE |  | 100 |  |  | 214 |  |  | 267 | 268 | 0 | 0 | 0 | 255 | 253 | 256 | 254 | 256 | 255 | 239 | 238 | 239 | 2.3 | 4.7 | 5.8 | 0.5 | 0.9 | 1.3 | 0 | 0.2 | 0 | 0.5 | 1 | 1.3 | 8 | 16 | 20 | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | The UPS only use one bank and one breaker. Everything is in good condition. This ups also use two module. |  | 22778 |  | 7110 | KLMFEP-33001
| SC_PM_NA_UPS_NA (4).pdf | KLS | 14/01/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 34.2 | 40.9 | 101 |  |  | 268 | 268 | 0 | 0 | 0 | 256 | 256 | 258 | 256 | 256 | 257 |  |  |  | 4.9 | 7.6 | 11.8 | 1.1 | 1.9 | 2.8 | 0.3 | 0.6 | 0.5 | 1.2 | 1.8 | 2.8 | 17 | 27 | 40 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipment is in good condition |  | 19898 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_2.pdf | KLS | 14/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 | 38.2 | 270 | 50 | 50 | 268 | 263 | 0 | 0 | 0 | 234 | 233 | 235 | 236 | 334 | 239 | 240 | 240 | 240 | 1.6 | 4.7 | 3.7 | 0.4 | 1 | 0.8 | 0 | 0.2 | 0.1 | 0.3 | 1.1 | 0.8 | 5 | 15 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.8 | 12.6 | 12.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 200 | 100 | 100 | 50 | 100 | all equipment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_1.pdf | KLS | 14/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 24 |  | 240 |  |  | 260 | 261 | 0 | 0 | 0 | 271 | 272 | 273 | 240 | 241 | 242 | 1.5 | 1.4 | 1.3 | 0.3 | 1.2 | 0.4 | 0.3 | 0.1 | 0.9 | 0.1 | 0.1 | 0 | 0.2 | 1 | 1 | 5 | 14 | 9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.4 | 12.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | 240 | 100 | 120 | 50 | 120 | OK |  | 7110 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA (3).pdf | KLS | 2023-04-07 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 65 |  | 105 | 50 | 50 | 268 | 268 | 0 | 0 | 0 | 254 | 254 | 255 | 254 | 254 | 255 | 240 | 239 | 239 | 4.8 | 7.6 | 11.5 | 1.1 | 1.8 | 2 | 0.3 | 0.5 | 0.4 | 1.1 | 1.9 | 2.7 | 17 | 28 | 45 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | good condition |  | 7223 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_14.pdf | OCC | [83 empty] | KLMFEP-33001

## snc
workorder_id | filename | station | date_time | pm_order | checklist_items.safety_and_preparation.make_sure_safety_precautions_procedures_being_followed_as_required..status | checklist_items.safety_and_preparation.inform_occ_before_start_any_task..status | checklist_items.general_inspection.perform_visual_inspection_and_confirm_all_cable_properly_connected..status | checklist_items.general_inspection.confirm_both_of_module_is_on_and_inverter_mode..status | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.status | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.A_battery_capacity | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.B_module_temp.in | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.B_module_temp.out | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.C_battery_run_time | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.D_output_freq_hz | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.E_bypass_freq_hz | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.F_battery_voltage_v.positive | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.F_battery_voltage_v.negative | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.G_battery_charge_car_a.positive | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.G_battery_charge_car_a.negative | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.H_discharge_current_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.I_rectifier_voltage_v_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.I_rectifier_voltage_v_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.I_rectifier_voltage_v_c | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.J_bypass_voltage_v_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.J_bypass_voltage_v_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.J_bypass_voltage_v_c | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.K_output_voltage_v_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.K_output_voltage_v_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.K_output_voltage_v_c | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.L_output_current_a_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.L_output_current_a_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.L_output_current_a_c | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.M_active_power_kw_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.M_active_power_kw_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.M_active_power_kw_c | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.N_reactive_power_kva_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.N_reactive_power_kva_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.N_reactive_power_kva_c | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.O_apparent_power_kva_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.O_apparent_power_kva_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.O_apparent_power_kva_c | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.P_output_power_percent_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.P_output_power_percent_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.P_output_power_percent_c | checklist_items.servicing_and_cleaning.set_the_ups_to_maintenance_bypass_mode_by_using_command_from_module..status | checklist_items.servicing_and_cleaning.switching_on_switch_maintenance_bypass_in_front_of_ups_rack..status | checklist_items.servicing_and_cleaning.confirm_the_display_panel_is_showing_bypass_mode..status | checklist_items.servicing_and_cleaning.switch_off_all_battery_breakers..status | checklist_items.servicing_and_cleaning.switch_off_both_of_module_using_2_finger_push_button_on_off..status | checklist_items.servicing_and_cleaning.open_screw_and_pull_both_of_module_to_cleaning..status | checklist_items.servicing_and_cleaning.open_screws_each_battery_bank_and_check_the_voltage..status | checklist_items.servicing_and_cleaning.wait_for_the_electrolytic_condensers_on_the_power_board_to_discharge_wait_at_least_15min_before_proceed_any_maintenance_work..status | checklist_items.servicing_and_cleaning.h.battery_readings.battery1 | checklist_items.servicing_and_cleaning.h.battery_readings.battery2 | checklist_items.servicing_and_cleaning.h.battery_readings.battery3 | checklist_items.servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries._ensure_minimum_voltage_is_read_as_12v_and_maximum_should_not_be_more_than_13.8v..status | checklist_items.servicing_and_cleaning.j.status | checklist_items.servicing_and_cleaning.check_end_to_end_batteries_voltages..status | checklist_items.servicing_and_cleaning.do_the_cleaning_on_all_the_batteries._confirm_and_ensure_no_cable_is_disconnected_from_any_terminals..status | checklist_items.servicing_and_cleaning.m.status | checklist_items.servicing_and_cleaning.n.status | checklist_items.servicing_and_cleaning.after_completed_the_cleaning_confirm_all_cablings_are_secured_and_in_the_correct_position..status | checklist_items.servicing_and_cleaning.switch_on_both_of_module_using_2_finger_push_button_on_off..status | checklist_items.servicing_and_cleaning.button_on_off..status | checklist_items.servicing_and_cleaning.normalized_all_battery_breakers..status | checklist_items.servicing_and_cleaning.switch_off_switch_maintenance_bypass_in_front_of_ups_rack..status | checklist_items.servicing_and_cleaning.set_the_ups_to_inverter_mode_by_using_command_from_module..status | checklist_items.servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada..status | checklist_items.servicing_and_cleaning.check_and_see_is_everything_back_to_normal..status | checklist_items.battery_backup_test.before_proceed_this_test_make_sure_battery_level_should_be_above_80%_of_load..status | checklist_items.battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated..status | checklist_items.battery_backup_test.turn_off_main_switch_breaker_for_main_incoming_supply..status | checklist_items.battery_backup_test.confirm_after_a_few_seconds_alarm_sounding_"battery_working"_led_illuminate_and_ups_change_to_"battery_mode"..status | checklist_items.battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage..status | checklist_items.battery_backup_test.switch_on_back_main_switch_breaker_after_ups_reaching_50%_of_battery_level..status | checklist_items.battery_backup_test.battery_backup_test.before.time_minutes | checklist_items.battery_backup_test.battery_backup_test.before.battery_percentage | checklist_items.battery_backup_test.battery_backup_test.after.time_minutes | checklist_items.battery_backup_test.battery_backup_test.after.battery_percentage | checklist_items.battery_backup_test.battery_backup_test.battery_backup_time_minutes | comments_recommendation | performed_by.name | performed_by.id | verified_by.name | verified_by.id | reference_document
| SC_PM_NA_UPS_NA_1 (3).pdf | OCC | 27/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 26.6 | 32 | 180 | 50 | 50 | 267 | 268 |  |  | 0 | 247 | 247 | 247 | 247 | 247 | 245 | 230 | 230.9 | 230 |  | 3.5 | 4.3 | 2.3 | 2.9 | 3.4 | 6.6 | 0.7 | 1 | 0.6 | 0.7 | 1.2 | 0.03 | 0.89 | 0.84 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.3 | 13.3 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | UPS GOOD CONDITION |  | 7248 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_12.pdf | OCC | 27/07/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 629 |  |  | 267 | 267 |  |  |  | 250 | 249 | 249 | 251 | 249 | 248 | 231 | 231 | 231 | 13 | 14 | 17 | 2.9 | 3 | 3.8 | 1.1 | 1.3 | 1.7 | 3 | 3.4 | 3.1 | 23 | 25 | 31 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Battery run test in good condition |  | 20826 |  | 7110 | KLMFEP-33001
| SC_PM_NA_UPS_NA_2 (2).pdf | OCC | 27/04/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 26.6 | 32 | 180 | 50 | 50 | 267 | 268 | 0 | 0 | 0 | 247 | 247 | 247 | 247 | 247 | 245 | 230 | 230.9 | 230 | 2.3 | 3.5 | 4.3 | 2.3 | 2.9 | 3.4 | 0.6 | 0.7 | 1.1 | 0.6 | 0.7 | 1.2 | 0.03 | 0.89 | 0.84 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12 | 12 | 12 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 180 |  |  | 7248 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_3 (1).pdf | DCC | 26/07/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 |  |  | 50 | 50 | 272 | 272 |  |  | 0 | 246 | 245 | 247 | 246 | 246 | 246 | 240 | 240 | 240 | 37.7 | 40.1 | 36.7 | 7.7 | 7.6 | 8.1 | 8.7 | 8.6 | 8.8 | 96.4 | 98.6 | 102.3 |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [11 empty] | Cannot do battery run test due to battery cannot support high load equipment. | SYAZUAN | 19921 | MOHD RAZIF | 7222 | KLMFEP-33001
4000555059 | SC_PM_QTR_UPS_4000555059.pdf | DCC | 26/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 |  |  | 50 | 50 | 272 | 272 | 0 | 0 |  |  |  |  | 240 | 242 | 243 | 243 | 243 | 243 | 40 | 39 | 42 | [9 empty] | 5.7 | 8.7 | 8.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE |  | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [11 empty] | du not back up test, don't have spare batter, ups temporary in half condition, ups error battery faulty |  | 7248 |  | 7111 | KLMFEP-33001
4000493765 | SC_PM_QTR_UPS_4000493765.pdf | DCC | 26/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 26 |  |  | 50 | 50 | 272 | 272 | [6 empty] | 240 | 242 | 243 | 243 | 243 | 243 | 40 | 39 | 42 | [9 empty] | 8.7 | 8.7 |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.2 | 13.6 | 13.8 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | 100 | 20 | 50 | 20 | all equipment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
4000597742 | SC_PM_QTR_UPS_4000597742_1.pdf | DCC | 2024-01-26 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 |  |  |  |  | 272 | 272 | 0 | 0 |  |  |  |  | 245 |  |  | 228 |  |  | 39.5 | [14 empty] | TRUE | TRUE | [5 empty] | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | [6 empty] | TRUE | TRUE | TRUE |  | TRUE | [9 empty] | UPS in a good condition. I unit bateri voltage 25 | KARNA |  | AZHAR YUNUS | 7111 | KLMFEP-33001
4000555059 | SC_PM_QTR_UPS_4000555059_1.pdf | DCC | 26/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 |  |  | 50 | 50 | 272 | 271 | 0 | 0 |  |  |  |  | 240 | 242 | 243 | 243 | 243 | 243 | 40 | 39 | 42 | [9 empty] | 5.7 | 8.7 | 8.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | TRUE | [5 empty] | UPS error battery faulty do not backup tes, ups temporary in half in dition, dant have spare battery. |  | 7110 |  | 7111 | KLMFEP-33001
4000480679 | SC_PM_QTR_UPS_4000480679.pdf | DCC | 26/07/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 |  |  |  |  | 272 | 272 | [6 empty] | 242 |  |  | 239 |  |  | 39.7 | [14 empty] | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.2 | 13.4 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | 100 | 20 | 50 | 20 | not display time estimate | SYAHRUL AZWAN | 7110 | AZHAR YUNUS | 7111 | KLMFEP-33001
4000608031 | SC_PM_QTR_UPS_4000608031.pdf | DCC | 26/04/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 |  |  | 50 | 50 | 272 | 272 |  |  | 0 | 246 | 245 | 247 | 246 | 246 | 246 | 240 | 240 | 240 | 37.7 | 40.1 | 36.7 | 7.7 | 7.6 | 8.1 | 8.7 | 8.6 | 8.8 | 96.4 | 98.6 | 102.3 |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [11 empty] | cant do battery run test because battery cannot support high load equipment |  | 21048 |  | 7111 | KLMFEP-33001
4000530701 | SC_PM_QTR_UPS_4000530701.pdf | OCC | 26/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 |  | 180 | 50 | 50 | 267 | 267 | 0 | 0.1 | 0 |  |  |  | 247 | 247 | 246 | 230 | 230 | 230 | 24 | 29 | 5.2 | 0.5 | 0.6 | 1.1 | 0.6 | 0.7 | 1.2 | 0.6 | 0.7 | 1.2 | 0.83 | 0.89 | 0.83 | [8 empty] | 12 | 12 | 12 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 100 |  |  | 7222 |  | 7111 | KLMFEP-33001
4000467077 | SC_PM_QTR_UPS_4000467077.pdf | DCC | 26/04/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 40.1 | 38.8 | 349 | 19 | 50 | 267 | 268 | 0 | 0 | 0 | 298 | 248 | 247 | 230 | 227 | 277 | 5.3 | 5.5 | 1.3 | 1.2 | 1.2 | 2.3 | 0.3 | 0.1 | 0.4 | 0.3 | 0.1 | 0.4 | 1.2 | 1.2 | 2.2 | 19 | 10 | 37 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.6 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | 100 | 15 | 50 | 15 | not displaayed time astimate |  | 14952 |  | 7111 | KLMFEP-33001
4000669120 | SC_PM_QTR_UPS_4000669120.pdf | DCC | 26/01/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 50 | 50 | 50 | 268 | 268 | 0 | 0 | 0 | 242 | 242 | 245 | 242 |  |  | 240 |  |  | 38.5 |  |  | 8.6 |  |  | 3.7 |  |  | 8.9 | [5 empty] | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [10 empty] | KLMFEP-33001
4000597742 | SC_PM_QTR_UPS_4000597742.pdf | DCC | 26/01/2024 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | [5 empty] | 272 | 272 | 0 | 0 |  |  |  |  | 245 |  |  | 238 | [17 empty] | TRUE | [7 empty] | 13.5 | 13.8 | 25 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [6 empty] | TRUE | TRUE |  | TRUE | [9 empty] | Ups in a good condition. I unit bateri voltage 25V |  | 7262 |  | 7111 | KLMFEP-33001
4000509113 | SC_PM_QTR_UPS_4000509113.pdf | OCC | 26/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 |  |  | 50 | 50 | 272 | 272 | 0 | 0 |  |  |  |  | 240 | 242 | 243 | 243 | 243 | 243 | 4 | 3.9 | 4.2 | [9 empty] | 5.7 | 8.7 | 8.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.9 | 12.9 | 12.8 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | 100 | 20 | 50 | 20 | Good Condition |  | 7223 |  | 7111 | KLMFEP-33001
4000446356 | SC_PM_QTR_UPS_4000446356.pdf | DCC | 26/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 40.1 | 38.8 | 349 | 49 | 50 | 267 | 268 | 0 | 0 | 0 | 248 | 248 | 247 | 249 | 248 | 248 | 230 | 238 | 239 | 5.3 | 5.5 | 10.7 | 1.2 | 1.2 | 2.3 | 0.3 | 0.1 | 0.4 | 1.2 | 1.2 | 2.2 | 19 | 10 | 35 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.6 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | 100 | 15 | 50 | 15 | equitment in good conditions but not view or display estimate time back up, -battery drain out very fast |  | 11727 |  | 7111 | KLMFEP-33001
4000647402 | SC_PM_QTR_UPS_4000647402.pdf | OCC | 25/10/2024 | 4000647402 | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 21.0 | 23.3 |  |  |  | 267 | 267 | 0.1 | 0.1 |  | 246 | 245 | 245 | 247 | 246 | 244 | 231 | 231 | 231 | 11 | 13.1 | 19.3 | 2.2 | 2.7 | 4.1 | 2.5 | 3 | 4.5 | 1 | 1.1 | 1.6 | 18.5 | 23 | 34.1 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All battery in good condition: |  | 22153 |  | 7222 | KLMFEP-33001
4000576167 | SC_PM_QTR_UPS_4000576167.pdf | OCC | 25/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 26.6 | 32 | 180 | 50 | 50 | 267 | 268 | 0 | 0 | 0 | 247 | 247 | 244 | 247 | 247 | 245 | 230 | 230.9 | 230 | 2.8 | 3.5 | 4.3 | 2.3 | 2.9 | 3.4 | 0.6 | 0.7 | 1.1 | 0.6 | 0.7 | 1.2 | 0.03 | 0.89 | 0.84 |  | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | 13.5 | 13.3 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 195 | 100 | 15 |  |  | ups good Condition |  | 7262 |  | 7111 | KLMFEP-33001
4000493787 | SC_PM_QTR_UPS_4000493787.pdf | OCC | 25/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 32.5 |  | 180 | 49.9 | 49.97 | 247 | 247 | 0 | 0 | 0 |  |  |  | 247 | 246 | 245 | 230 | 230 | 230 | 2.4 | 3.1 | 5 | 0.5 | 0.6 | 0.2 | 2.1 | 2.8 | 4.2 |  |  |  | 0.8 | 0.9 | 0.9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.8 | 13 | 12.8 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 180 | all equipment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
4000615391 | SC_PM_QTR_UPS_4000615391.pdf | OCC | 25/07/2024 | 4000615391 | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 26.7 |  | 170 |  |  | 266 | 267 | 0 | 0 | 0 | 247 | 247 | 247 | 246 | 247 | 246 | 230 | 230 | 230 | 2.3 | 3.5 | 4.3 | 2.3 | 2.9 | 3.4 | 0.6 | 0.7 | 1.1 | 6.6 | 0.7 | 1.2 | 0.03 | 0.89 | 0.85 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | ups In good condition |  | 22278 |  | 7222 | KLMFEP-33001
4000555086 | SC_PM_QTR_UPS_4000555086.pdf | OCC | 25/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 |  | 180 | 80 | 50 | 267 | 267 | 0 | 0.1 | 0 | 347 | 247 | 244 | 247 | 247 | 246 | 230 | 230 | 230 | 2.4 | 2.9 | 1.1 | 0.6 | 0.7 | 1.2 | 0.6 | 0.7 | 1.2 | 0.6 | 0.7 | 1.2 | 0.83 | 0.84 | 0.83 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | - ups in good condition |  | 7110 |  | 7111 | KLMFEP-33001
4000608059 | SC_PM_QTR_UPS_4000608059.pdf | OCC | 25/04/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 629 |  |  | 267 | 267 |  |  |  | 250 | 249 | 249 | 251 | 249 | 248 | 231 | 231 | 231 | 13 | 14 | 17 | 2.9 | 3 | 3.8 | 1.1 | 1.3 | 1.7 | 3 | 3.4 | 3.1 | 23 | 25 | 31 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Battery run test in good condition. |  | 21048 |  | 7111 | KLMFEP-33001
4000530675 | SC_PM_QTR_UPS_4000530675.pdf | DCC | 25/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 |  |  | 50 | 50 | 272 | 272 | 0 | 0 |  |  |  |  | 240 | 242 | 243 | 243 | 243 | 243 | 40 | 39 | 42 | [9 empty] | 7.7 | 8.7 | 8.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.9 | 12.7 | 12.8 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | 100 | 20 | 50 | 20 |  |  | 7222 |  | 7111 | KLMFEP-33001
4000467097 | SC_PM_QTR_UPS_4000467097.pdf | OCC | 25/04/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 24.7 | 22.6 | 153 | 49.9 | 49.6 | 261 | 267 | 268 | 288 | 1.3 |  |  |  | 244 | 243 | 243 | 241 | 241 | 214 | 0.2 | 2.1 | 2.8 | 0.4 | 0.2 | 2.4 | 0.5 | 0.2 | 0.5 | 0.5 | 1.4 | 2.6 | 7 | 23 | 36 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.4 | 13.4 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 20 | 100 | 50 | 50 | 20 | ok |  | 14952 |  | 7111 | KLMFEP-33001
4000509061 | SC_PM_QTR_UPS_4000509061.pdf | OCC | 25/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 |  | 180 |  |  | 267 | 267 | 0 | 0.1 | 0 |  |  |  | 247 | 247 | 246 | 230 | 230 | 230 | 24 | 29 | 5.2 | 0.5 | 0.6 | 1.2 | 0.6 | 0.7 | 1.2 | 0.6 | 0.7 | 1.2 | 0.83 | 0.89 | 0.93 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12 | 12 | 12 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 180 | GOOD CONDITION |  | 7223 |  | 7111 | KLMFEP-33001
4000446335 | SC_PM_QTR_UPS_4000446335.pdf | OCC | 25/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 48.1 | 37.8 | 270 | 50 | 49.9 | 207 | 240 | 0 | 0 | 0 | 248 | 248 | 248 | 249 | 249 | 239 | 238 | 238 | 239 | 5.3 | 5.3 | 10.2 | 1.2 | 1.2 | 2.3 | 0.3 | 0.1 | 0.4 | 1.2 | 1.2 | 2.5 | 14 | 18 | 36 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.6 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 80 | all equitment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
4000480717 | SC_PM_QTR_UPS_4000480717.pdf | TSA | 24/04/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 42 |  | 185 |  |  | 212 | 268 | 0 | 0 | 0 | 238 | 237 | 240 | 238 | 239 | 240 | 240 | 241 | 244 | 1.6 | 1.5 | 4.4 | 0.3 | 1.2 | 1 | 0.1 | 0.1 | 0.2 | 0.4 | 1.3 | 1 | 5 | 17 | 15 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.6 | 13.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 90 | ok. | MOHD RAZIF | 7222 | AZHAR YUNUS | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA (7).pdf | TSA | 24/10/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 27.8 | 28.9 | 210 |  |  | 266 | 266 | 0 | 0 | 0 | 241 | 240 | 243 | 241 | 240 | 242 |  |  |  | 1.4 | 5.3 | 6 | 0.3 | 1.1 | 1.3 | 0.1 | 0.2 | 0.4 | 0.3 | 1.1 | 1.4 | 5 | 20 | 21 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipment are in good condition. |  | 20005 |  | 7248 | KLMFEP-33001
4000576188 | SC_PM_QTR_UPS_4000576188.pdf | TSA | 24/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.0 | 39.1 | 228 | 50.04 | 50 | 266 | 266 | 0 | 0 | 0 | 234 | 236 | 237 | 234 | 236 | 237 | 240 | 239 | 240 | 1.2 | 4.2 | 5.4 | 0.3 | 1 | 1.2 | 0 | 0 | 0.3 | 0.3 | 1 | 1.2 | 4 | 14 | 20 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | 100 |  |  | 228 | All Good Condition |  | 7262 |  | 7111 | KLMFEP-33001
4000509052 | SC_PM_QTR_UPS_4000509052.pdf | TSA | 24/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 | 33 | 207 | 50 | 50 | 266 | 266 | 0 | 0 | 0 | 237 | 238 | 240 | 237 | 238 | 240 | 240 | 239 | 240 | 1 | 4.8 | 6.2 | 0.2 | 1.3 | 1.4 | 0.1 | 0.1 | 0.3 | 0.2 | 1.2 | 1.4 | 3 | 19 | 21 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.5 | 12.8 | 12.8 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 180 | 2 batery faulty and all equipment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_9.pdf | TSA | 24/07/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.7 | 40.2 | 210 |  |  | 266 | 266 | 0 | 0 | 0 | 237 | 239 | 240 | 237 | 239 | 24 |  |  |  | 1.3 | 4.5 | 5.6 | 0.3 | 1.1 | 1.3 | 0 | 0 | 0.3 | 0.3 | 1.1 | 1.3 | 4 | 17 | 20 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 53.7 | 53.6 | 53.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Battery & Module in good condition. |  | 19921 |  | 7222 | KLMFEP-33001
4000555036 | SC_PM_QTR_UPS_4000555036.pdf | BAS | 24/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.5 | 38.4 | 225 | 50 | 50 | 266 | 266 | 0 | 0 | 0 | 249 | 249 | 249 | 249 | 249 | 260 | 240 | 240 | 240 | 1.5 | 3.8 | 6 | 0.3 | 0.8 | 1.4 | 0 | 0 | 0.2 | 1.3 | 0.8 | 1.4 | 5 | 12 | 32 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [7 empty] | 7222 |  | 7111 | KLMFEP-33001
4000555099 | SC_PM_QTR_UPS_4000555099.pdf | TSA | 24/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 32.7 | 39.3 | 235 | 50 | 50 | 266 | 206 | 0 | 0 | 0 | 235 | 236 | 237 | 240 | 239 | 240 | 1.4 | 4.8 | 5.1 | 0.3 | 1 | 1.2 | 0 | 0.1 | 0.3 | 0 | 0.1 | 0.3 | 0.3 | 1 | 1.2 | 5 | 15 | 18 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All batery in good condition. connection cable and inficator module good condition |  | 7110 |  | 7111 | KLMFEP-33001
4000480715 | SC_PM_QTR_UPS_4000480715.pdf | TSA | 24/07/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.9 | 40.5 | 290 |  |  | 266 | 266 | 0 | 0 | 0 | 240 | 241 | 243 | 240 | 241 | 242 | 240 | 239 | 240 | 1 | 4.1 | 4.9 | 0.2 | 1 | 1.1 | 0 | 0 | 0.2 | 0.2 | 1 | 1.2 | 4 | 16 | 17 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.4 | 13.3 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 540 | 100 |  |  |  | ups faulty\alarm battery discharge appear\must battery broken emporary maintanance bypass | SYAHRUL AZWAN | 7110 | AZHAR YUNUS | 7111 | KLMFEP-33001
4000608074 | SC_PM_QTR_UPS_4000608074.pdf | TSA | 2024-04-24 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 33.7 | 40.1 | 218 |  |  | 266 | 266 | 0 | 0 | 0 | 236 | 239 | 241 | 236 | 239 | 241 | 240 | 239 | 240 | 1.6 | 5.5 | 6.1 | 0.3 | 1.3 | 1.3 | 0.1 | 0.1 | 0.3 | 0.4 | 1.2 | 1.3 | 5 | 20 | 21 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | -Hardware In good condition |  | 20079 |  | 7111 | KLMFEP-33001
4000530710 | SC_PM_QTR_UPS_4000530710.pdf | TSA | 24/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28.0 | 33.0 | 196.2 |  |  | 266 | 266 | 0 | 0.6 | 0 | 237 | 238 | 240 | 237 | 238 | 260 | 240 | 259 | 240 | 1 | 4.8 | 6.2 | 0.2 | 1.2 | 1.7 | 0.1 | 0.1 | 0.3 | 0.2 | 1.2 | 1.4 | 3 | 19 | 21 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.5 |  | 12.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 180 | good Condition |  | 7110 |  | 7111 | KLMFEP-33001
4000668040 | SC_PM_QTR_UPS_4000668040.pdf | TSA | 24/01/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 29.9 | 35.9 | 204 |  |  | 266 | 266 | 0 | 0 | 0 | 239 | 241 | 243 | 240 | 241 | 243 | 240 | 239 | 239 | 1.5 | 5.5 | 6.2 | 0.3 | 1.2 | 1.4 | 0.1 | 0.2 | 0.4 | 0.3 | 1.1 | 1.4 | 5 | 20 | 21 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | UPS IN GOOD CONDITION |  | 22876 |  | 7110 | KLMFEP-33001
4000597870 | SC_PM_QTR_UPS_4000597870.pdf | TSA | 24/01/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.0 | 39.1 | 228 | 50.04 | 50 | 266 | 266 | 0 | 0 | 0 | 234 | 236 | 237 | 234 | 236 | 237 | 240 | 239 | 240 | 1.2 | 4.3 | 5.4 | 0.3 | 1 | 1.2 | 0 | 0 | 0.3 | 0.3 | 1 | 1.2 | 4 | 14 | 20 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All good condition |  | 7248 |  | 7111 | KLMFEP-33001
4000509053 | SC_PM_QTR_UPS_4000509053.pdf | TSA | 24/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28.0 | 33.0 | 207 |  |  | 266 | 266 | 0 | 0 | 0 | 237 | 238 | 240 | 237 | 238 | 240 | 240 | 239 | 240 | 1.07 | 48 | 6.2 | 0.2 | 1.3 | 1.4 | 0.1 | 0.1 | 0.3 | 0.2 | 1.2 | 1.4 | 3 | 19 | 21 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.5 | 12.7 | 12.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 180 | Good Condition |  | 7223 |  | 7111 | KLMFEP-33001
4000446312 | SC_PM_QTR_UPS_4000446312.pdf | TSA | 24/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 42 |  | 185 | 30 | 50 | 272 | 268 | 0 | 0 | 0 | 238 | 237 | 240 | 238 | 239 | 240 | 240 | 241 | 244 | 1.6 | 1.3 | 4.4 | 0.3 | 1.2 | 1 | 0.1 | 0.1 | 0.2 | 0.4 | 1.3 | 1 | 5 | 17 | 15 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.6 | 13.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 200 | 100 | 110 | 80 | 110 | all equitment in good conditions. |  |  |  | 7111 | KLMFEP-33001
4000480674 | SC_PM_QTR_UPS_4000480674.pdf | CIT | 2023-07-23 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 30 | 37.9 | 383 |  |  | 266 | 268 | 0 | 0 | 0 | 239 | 240 | 241 | 240 | 239 | 241 | 240 | 239 | 239 | 240 | 239 | 239 | 1.1 | 1.9 | 3.9 | 0.2 | 0.5 | 0.9 | 0.1 | 0 | 0.1 | 0.2 | 0.5 | 0.9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.7 | 13.5 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 380 | 100 | 180 | 50 | 150 | Ok | SYAHRUL AZWAN | 7110 | AZHAR YUNUS | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_7.pdf | CIT | 23/11/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 30.2 | 34.5 | 377 |  |  | 266 | 268 | 0 | 0.1 | 0 | 245 | 243 | 246 | 245 | 243 | 247 |  |  |  | 1.2 | 2 | 3.9 | 0.2 | 0.5 | 0.9 | 0.1 | 0.1 | 0.1 | 0.3 | 0.4 | 0.9 | 4 | 7 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | ALL EQUIPMENTS ARE IN GOOD CONDITION |  | 21970 |  | 7223 | KLMFEP-33001
4000646748 | SC_PM_QTR_UPS_4000646748.pdf | CIT | 23/10/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 34.5 | 37.5 | 379 |  |  | 266 | 268 | 0 | 0.1 | 0 | 299 | 248 | 250 | 299 | 247 | 250 | 240 | 239 | 239 | 1.2 | 1.9 | 3.6 | 0.2 | 0.5 | 0.8 | 0.1 | 0.1 | 0.1 | 0.2 | 0.5 | 0.9 | 4 | 6 | 13 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | replace for unit new battery-madule in good condition |  | 19925 |  | 7256 | KLMFEP-33001
4000576119 | SC_PM_QTR_UPS_4000576119.pdf | CIT | 23/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 38 |  | 365 | 50.03 | 50 | 266 | 268 | 0 | 0.1 | 0 | 250 | 249 | 250 | 250 | 249 | 251 | 239 | 239 | 239 | 1.3 | 2 | 3.9 | 0.2 | 0.4 | 0.9 | 0.1 | 0.1 | 0.2 | 0.3 | 0.5 | 0.9 | 4 | 6 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Time For both module not same Module 1 2h 25m and module 2 6h 5m |  | 7110 |  | 7111 | KLMFEP-33001
4000493761 | SC_PM_QTR_UPS_4000493761.pdf | CIT | 23/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28.5 | 35.0 | 376 |  |  | 266 | 268 | 0 | 0.1 | 0 | 248 | 247 | 245 | 248 | 247 | 249 | 240 | 240 | 239 | 1.1 | 2.1 | 4.1 | 0.2 | 0.4 | 0.9 | 0 | 1 | 0 | 0.2 | 0.4 | 0.9 | 4 | 6 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.8 | 12.7 | 12.8 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 380 | 100 | 180 | 50 | 180 | all equipment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
4000660367 | SC_PM_QTR_UPS_4000660367.pdf | CIT | 2025-01-23 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 27.7 | 33.8 | 377 |  |  | 266 | 268 | 0 | 0.1 | 0 | 246 | 245 | 247 | 246 | 245 | 248 | 239 | 239 | 239 | 1.1 | 2.2 | 3.6 | 0.2 | 0.4 | 0.8 | 1 | 0 | 0.1 | 0.3 | 0.4 | 0.8 | 4 | 7 | 13 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | UPS in a good condition. |  | 22777 |  | 7222 | KLMFEP-33001
4000555052 | SC_PM_QTR_UPS_4000555052.pdf | CIT | 23/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 110 | 37 |  | 165 | 50 | 50 | 272 | 272 | 0 | 0 | 0 | 244 |  |  | 244 | 243 | 244 | 239 | 239 | 239 | 2.6 | 6.2 | 6.8 | 0.6 | 1.3 | 1.6 | 0 | 0.1 | 0.2 | 0.6 | 1.2 | 1.7 | 9 | 19 | 25 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [7 empty] | 7222 |  | 7111 | KLMFEP-33001
4000608023 | SC_PM_QTR_UPS_4000608023.pdf | CIT | 23/04/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28.2 | 34.9 | 369 | 50.4 | 50 | 266 | 268 | 0 | 0.1 | 0 | 249 | 248 | 250 | 249 | 248 | 250 | 240 | 239 | 239 | 1.3 | 1.8 | 3.9 | 0.3 | 0.4 | 0.9 | 0.1 | 0.1 | 0.2 | 0.3 | 0.4 | 0.9 | 5 | 6 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | (D01-D10) 1 battery faulty |  | 21048 |  | 7111 | KLMFEP-33001
4000530672 | SC_PM_QTR_UPS_4000530672.pdf | CIT | 23/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28.5 | 35.0 | 375 |  |  | 266 | 268 | 0.8 | 0.1 | 0 | 248 | 247 | 245 | 248 | 247 | 249 | 240 | 240 | 235 | 1.1 | 2.1 | 4.1 | 0.2 | 0.4 | 0.9 | 0.1 | 1 | 0.1 | 0.2 | 0.4 | 0.9 | 4 | 6 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.5 | 12.6 | 12.8 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 81 | 100 | 180 | 10 | 180 | Good Condition |  | 7110 |  | 7111 | KLMFEP-33001
4000467073 | SC_PM_QTR_UPS_4000467073.pdf | CIT | 23/04/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 37.1 | 44.8 | 307 |  |  | 268 | 268 | 0 | 0.1 | 0 | 242 | 242 | 249 | 248 | 249 | 240 | 241 | 239 | 239 | 1 | 2 | 3 | 0.2 | 0.4 | 0.7 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.7 | 3 | 2 | 11 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.4 | 13.2 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 160 | 100 | 80 | 50 | 80 | ok |  | 7222 |  | 7111 | KLMFEP-33001
4000597714 | SC_PM_QTR_UPS_4000597714.pdf | CIT | 23/01/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 35.4 | 42.5 | 169 | 50.05 | 50 | 272 | 266 | 0 | 0 | 0 | 246 | 246 | 248 | 247 | 246 | 248 | 240 | 240 | 240 | 2.6 | 5.7 | 7.3 | 0.6 | 1.4 | 1.6 | 0 | 0.1 | 0.2 | 0.6 | 1.3 | 1.7 | 10 | 18 | 24 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All EQUIPMENT IN A GOOD CONDITION |  | 7248 |  | 7111 | KLMFEP-33001
4000509117 | SC_PM_QTR_UPS_4000509117.pdf | CIT | 23/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28.5 | 35.0 | 375 |  |  | 266 | 268 | 0.8 | 0.1 | 0 | 248 | 247 | 245 | 248 | 247 | 244 |  |  |  | 1.1 | 2.1 | 4.1 | 2 | 0.4 | 0.9 | 0.1 | 10 | 0.1 | 0.2 | 0.4 | 0.9 | 4 | 6 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.5 | 12.6 | 12.8 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 180 | 50 | 180 |  |  | 7223 |  | 7111 | KLMFEP-33001
4000446359 | SC_PM_QTR_UPS_4000446359.pdf | CIT | 23/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 37.1 | 44.8 | 307 | 50 | 50 | 268 | 269 | 0 | 0.1 | 0 | 240 | 248 | 249 | 248 | 249 | 240 | 240 | 239 | 239 | 1 | 2 | 3 | 0.2 | 0.4 | 0.7 | 0.1 | 0 | 0.1 | 0.2 | 0.4 | 0.7 | 3 | 2 | 11 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.4 | 13.2 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 120 | 100 | 60 | 50 | 120 | ok |  | 7223 |  | 7111 | KLMFEP-33001
4000509068 | SC_PM_QTR_UPS_4000509068.pdf | MKU | 22/04/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36.6 | 42.6 | 306 |  |  | 262 | 262 | 0 | 0 | 0 | 243 | 242 | 244 | 243 | 242 | 244 | 240 | 240 | 240 | 1.4 | 3.3 | 3.6 | 0.3 | 0.7 | 0.78 | 0 | 0.1 | 0.2 | 0.3 | 0.8 | 0.8 | 5 | 12 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.4 | 12.6 | 12.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 160 | 100 | 80 | 150 | 80 | ok |  | 7222 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_1 (4).pdf | Mku | 22/11/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 37.3 |  | 238 | 50.04 | 50 | 268 | 268 | 0 | 0 | 0 | 238 | 238 | 239 | 238 | 238 | 239 | 239 | 239 | 240 | 1.6 | 5.3 | 3.8 | 0.3 | 1.2 | 1 | 0 | 0.3 | 0.2 | 0.3 | 1.2 | 0.9 | 5 | 19 | 15 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | ALL EQUIPMENT IN GOOD CONDITION |  | 7248 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_2 (3).pdf | MKU | 22/10/2024 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 32.5 |  | 259 | 50.05 | 50 | 268 | 268 | 0 | 0 | 0 | 237 | 236 | 238 | 237 | 237 | 239 | 240 | 240 | 239 | 1.6 | 4.4 | 3.7 | 0.3 | 1.1 | 0.8 | 0 | 0.2 | 0.1 | 0.4 | 1 | 1.8 | 5 | 16 | 12 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All battery in good condition and perform very well. |  | 11727 |  | 7256 | KLMFEP-33001
| SC_PM_NA_UPS_NA_3.pdf | Mku | 22/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 260 | 50 | 50 | 268 | 269 | 0 | 0 | 0 | 239 | 240 | 241 | 240 | 231 | 241 | 234 | 240 | 241 | 1.6 | 4.7 | 3.7 | 0.4 | 1 | 0.8 | 0 | 0.2 | 0.1 | 0.3 | 1.1 | 0.8 | 5 | 15 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | -all equipment in good condition -all cable tigth and secure |  | 7119 |  | 7111 | KLMFEP-33001
4000509070 | SC_PM_QTR_UPS_4000509070.pdf | MKU | 22/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.3 | 38.2 | 241 | 50 | 50 | 268 | 268 | 0 | 0 | 0 | 234 | 233 | 235 | 234 | 233 | 235 | 240 | 240 | 240 | 1.6 | 4.7 | 3.7 | 0.4 | 1 | 0.8 | 0 | 0.2 | 0.1 | 0.3 | 1.1 | 0.8 | 5 | 15 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.4 | 13.5 | 13.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 240 | 100 | 100 | 80 | 100 | Good Condition |  | 7223 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA (6).pdf | MKU | 22/07/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 29 | 33.5 | 265 |  |  | 26.9 | 26.9 | 0 | 0 | 0 | 237 | 236 | 240 | 237 | 236 | 240 |  |  |  | 1.45 | 4.5 | 3.5 | 0.3 | 1 | 0.8 | 0 | 0.2 | 0.1 | 0.3 | 1 | 0.8 | 5 | 17 | 13 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All batteries in good condition. |  | 22153 |  | 7223 | KLMFEP-33001
| SC_PM_NA_UPS_NA_2 (1).pdf | MKU | 22/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.3 | 38.2 | 260 | 50 | 50 | 218 | 268 | 0 | 0 | 0 | 234 | 233 | 235 | 234 | 233 | 235 | 240 | 240 | 240 | 1.6 | 4.7 | 3.7 | 0.4 | 1 | 0.8 | 0 | 0.2 | 0.1 | 0.3 | 1.1 | 0.8 | 5 | 15 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [7 empty] | 7222 |  | 7111 | KLMFEP-33001
4000509069 | SC_PM_QTR_UPS_4000509069.pdf | MKU | 22/07/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.2 | 37.9 | 247 | 50 | 50 | 265 | 269 | 0 | 0 | 0 | 237 | 237 | 239 | 237 | 236 | 234 | 240 | 240 | 239 | 1.6 | 4.5 | 3.7 | 0.3 | 1 | 0.9 | 0 | 0.2 | 0.1 | 0.3 | 1.1 | 0.8 | 5 | 16 | 12 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.6 | 13.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 240 | 100 | 100 | 50 | 200 | all equitment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_1 (5).pdf | MKU | 22/04/2024 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 22.5 | 23.8 | 238 | 50.03 |  | 268 | 268 | 0 | 0 | 0 | 240 | 236 | 242 | 240 | 238 | 242 |  |  |  | 1.6 | 5.1 | 4.3 | 0.3 | 1 | 0.8 | 0 | 0.4 | 0.4 | 0.3 | 1.2 | 1 | 5 | 18 | 15 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All batteries and module in good condition. |  | 19921 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA (2).pdf | MKU | 22/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.3 | 38.2 | 240 |  |  | 268 | 268 | 0 | 0 | 0 | 234 | 233 | 235 | 234 | 233 | 235 | 240 | 240 | 240 | 1.6 | 4.7 | 3.1 | 0.4 | 1 | 0.3 | 0 | 0.8 | 0.1 | 0.3 | 1.1 | 0.8 | 5 | 15 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.4 | 13.5 | 13.5 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 200 | 100 | 100 | 150 | 100 |  |  | 7110 |  | 7111 | KLMFEP-33001
4000669552 | SC_PM_QTR_UPS_4000669552.pdf | MKU | 22/01/2025 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 28.6 | 35.1 | 246 |  |  | 269 | 269 | 0 | 0 | 0 | 235 | 234 | 236 | 235 | 234 | 236 | 240 | 239 | 239 | 1.6 | 4.4 | 3.6 | 0.3 | 1 | 0.8 | 0.1 | 0.2 | 0.2 | 0.9 | 1 | 0.9 | 5 | 15 | 13 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | UPS in a good condition. |  | 22776 |  | 7222 | KLMFEP-33001
4000509072 | SC_PM_QTR_UPS_4000509072.pdf | Mku | 22/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.3 | 34.2 | 240 |  |  | 269 | 268 | 0 | 0 | 0 | 234 | 233 | 235 | 234 | 233 | 235 | 240 | 240 | 240 | 1.6 | 4.7 | 3.7 | 0.4 | 1.1 | 0.8 | 0 | 0.2 | 0.1 | 0.3 | 1.1 | 0.8 | 5 | 15 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.4 | 13.5 | 13.5 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 200 | 100 | 100 | 50 | 100 |  |  | 7222 |  | 7111 | KLMFEP-33001
4000509067 | SC_PM_QTR_UPS_4000509067.pdf | MKU | 22/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36.6 | 42.6 | 310 |  |  | 262 | 262 | 0 | 0 | 0 | 243 | 242 | 244 | 243 | 242 | 244 | 240 | 240 | 240 | 1.4 | 3.3 | 3.6 | 0.3 | 0.7 | 0.8 | 0 | 0.1 | 0.2 | 0.3 | 0.8 | 0 | 5 | 12 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.4 | 12.6 | 12.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 160 | 100 | 80 | 50 | 80 | OK |  | 7223 |  | 7111 | KLMFEP-33001
4000576104 | SC_PM_QTR_UPS_4000576104.pdf | BAS | 21/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 250 | 50.03 | 50 | 266 | 266 | 0 | 0 | 0 | 247 | 248 | 250 | 247 | 248 | 250 | 239 | 240 | 240 | 1.4 | 3.6 | 5.5 | 0.3 | 0.8 | 1.3 | 0 | 0.2 | 0.2 | 0.3 | 0.7 | 1.3 | 3 | 12 | 20 |  |  |  | TRUE | TRUE | TRUE | [30 empty] | All equipment in good condition |  | 20160 |  | 7111 | KLMFEP-33001
4000493753 | SC_PM_QTR_UPS_4000493753.pdf | BAS | 21/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.5 | 38.4 | 207 | 50 | 50 | 266 | 266 | 0 | 0 | 0 | 249 | 249 | 249 | 249 | 249 | 251 | 240 | 240 | 240 | 1.5 | 3.8 | 6 | 0.3 | 0.8 | 1.4 | 0 | 0 | 0.3 | 0.3 | 0.8 | 1.4 | 5 | 12 | 22 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.6 | 13.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 190 | 100 | 100 | 50 | 100 | Good Condition. | ROHIZAN | 7223 | AZHAR YUNUS | 7111 | KLMFEP-33001
4000597702 | SC_PM_QTR_UPS_4000597702.pdf | BAS | 21/01/2024 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 31.8 | 38.3 | 219 | 50 | 50 | 266 | 266 | 0 | 0 | 0 | 249 | 248 | 252 | 249 | 248 | 252 | 240 | 240 | 241 | 1.5 | 4.1 | 6 | 0.3 | 0.9 | 1.4 | 0 | 0.1 | 0.2 | 0.3 | 0.9 | 1.5 | 5 | 14 | 23 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | * Battery bank 1 and 2 (A01-040) need to be replaced. * Battery is damaged. * Battery can only cover 93% * Module P02 need to calibrate. |  | 20079 |  |  | KLMFEP-33001
| SC_PM_NA_UPS_NA_1 (6).pdf | BAS | 21/07/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28.3 | 32.9 | 268 |  |  | 266 | 266 | 0 | 0 | 0 | 248 | 247 | 252 | 248 | 247 | 252 |  |  |  | 1.3 | 2.9 | 5.1 | 0.3 | 0.6 | 1.1 | 0 | 0.1 | 0.1 | 0.3 | 0.7 | 1.1 | 4 | 11 | 17 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipment are in good condition. |  | 20005 |  | 7223 | KLMFEP-33001
4000480661 | SC_PM_QTR_UPS_4000480661.pdf | BAS | 21/07/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.3 | 38.3 | 228 |  |  | 266 | 206 | 0 | 0 | 0 | 249 | 249 | 249 | 249 | 249 | 252 | 240 | 240 | 240 | 1.5 | 3.8 | 6 | 3 | 9 | 1.4 | 0 | 0 | 0.3 | 0.3 | 0.8 | 1.4 | 5 | 13 | 22 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.6 | 13 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 190 | 100 | 100 | 50 | 100 | all equipment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
4000530660 | SC_PM_QTR_UPS_4000530660.pdf | BAS | 2023-04-21 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.5 | 38.4 | 225 |  |  | 266 | 266 | 0 | 0 | 0 | 249 | 249 | 249 | 249 | 249 | 250 | 240 | 240 | 240 | 1.5 | 3.8 | 6 | 0.3 | 0 | 1.4 | 0 | 0 | 0.3 | 0.3 | 0 | 1.4 | 5 | 12 | 22 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.6 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 200 | 100 | 100 | 50 | 100 |  |  | 7110 |  | 7111 | KLMFEP-33001
4000608011 | SC_PM_QTR_UPS_4000608011.pdf | BAS | 21/04/2024 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 33.1 |  | 238 | 50.03 | 50 | 266 | 266 | 0 | 0 | 0 | 249 | 248 | 251 | 248 | 249 | 252 | 240 | 239 | 240 | 1.5 | 3.4 | 5.6 | 0.3 | 0.8 | 1.3 | 0 | 0.1 | 0.2 | 0.3 | 0.8 | 1.4 | 5 | 12 | 20 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All module and batteries in good condition. Only using bank 3, bank 1 and 2 temporary doesn't have batteries due expired batteries. |  | 19921 |  | 7111 | KLMFEP-33001
4000467064 | SC_PM_QTR_UPS_4000467064.pdf | BAS | 21/04/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 29.3 | 36.6 | 272 |  |  | 267 | 268 | 1 | 0 | 0 | 248 | 248 | 250 | 248 | 248 | 254 | 240 | 240 | 240 | 1.5 | 3.5 | 4.5 | 0.3 | 0.7 | 1 | 0 | 0.1 | 0.1 | 0.3 | 0 | 1 | 8 | 11 | 16 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 120 | 12.9 | 13.2 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 80 | 50 | 80 | ok |  | 7110 |  | 7111 | KLMFEP-33001
4000660989 | SC_PM_QTR_UPS_4000660989.pdf | BAS | 21/01/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.1 | 39.8 | 243 |  |  | 266 | 266 | 0 | 0 | 0 | 246 | 247 | 249 | 246 | 246 | 249 | 241 | 230 | 240 | 1.4 | 3.1 | 5.6 | 0.3 | 0.7 | 0.2 | 0 | 0.2 | 0.1 | 0.3 | 0.8 | 1.3 | 5 | 12 | 19 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | # UPS in a good condition |  | 2276 |  | 7222 | KLMFEP-33001
4000509125 | SC_PM_QTR_UPS_4000509125.pdf | BAS | 21/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.5 | 38.4 | 225 | 50 | 50 | 266 | 266 | 0 | 0 | 0 | 249 | 249 | 249 | 249 | 249 | 250 | 240 | 240 | 240 | 1.5 | 3.8 | 6 | 0.3 | 0.8 | 1.4 | 0 | 0 | 0.3 | 0.3 | 0.8 | 1.4 | 5 | 12 | 22 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.6 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 200 | 100 | 100 | 50 | 100 |  |  | 7222 |  | 7111 | KLMFEP-33001
4000446126 | SC_PM_QTR_UPS_4000446126.pdf | BAS | 21/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 29.6 | 36.6 | 272 | 80 | 50 | 269 | 269 | 0 | 0 | 0 | 248 | 248 | 250 | 248 | 248 | 250 | 240 | 240 | 240 | 1.5 | 3.5 | 4.5 | 0.3 | 0.7 | 1 | 0 | 0.1 | 0.1 | 0.3 | 0.6 | 1 | 5 | 11 | 16 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.8 | 12.9 | 13.2 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 80 | 50 | 60 | ♡ |  | 7223 |  | 7111 | KLMFEP-33001
4000647410 | SC_PM_QTR_UPS_4000647410.pdf | RAN | 20/10/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 34.1 | 40.3 | 234 | 50.03 | 50 | 266 | 266 | 0 | 0 | 0 | 245 | 244 | 245 | 244 | 243 | 246 | 239 | 239 | 240 | 2.2 | 4 | 5.2 | 0.5 | 0.9 | 1.2 | 0 | 0.1 | 0.1 | 0.5 | 0.8 | 1.2 | 8 | 13 | 19 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Breaker 2 and 3 not function, waiting for new battery |  | 11727 |  | 7256 | KLMFEP-33001
4000576174 | SC_PM_QTR_UPS_4000576174.pdf | RAN | 20/10/2023 |  | TRUE | TRUE | TRUE | TRUE |  | 100 |  |  | 236 | 50.02 | 50 | 266 | 266 | 0 | 0 | 0 | 242 | 241 | 244 | 243 | 241 | 244 | 240 | 240 | 240 | 1.9 | 3.7 | 4.9 | 0.4 | 0.8 | 1.2 | 0 | 0.2 | 0.1 | 0.4 | 0.8 | 1.1 | 6 | 13 | 18 | TRUE | TRUE | TRUE | [33 empty] | All equipment in good condition |  | 20160 |  | 7111 | KLMFEP-33001
4000493784 | SC_PM_QTR_UPS_4000493784.pdf | RAN | 20/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 32.7 | 39.0 | 228 |  |  | 266 | 266 | 0 | 0.1 | 0 | 242 | 241 | 242 | 241 | 240 | 241 | 239 | 239 | 240 | 2.1 | 3.8 | 5.3 | 0.5 | 0.8 | 1.2 | 0 | 0.1 | 0.2 | 0.5 | 0.8 | 1.2 | 7 | 12 | 19 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.3 | 13.4 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 90 | Good Condition. |  | 7223 |  | 7111 | KLMFEP-33001
4000480709 | SC_PM_QTR_UPS_4000480709.pdf | RAN | 2022-07-20 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 34.5 | 40.6 | 217 |  |  | 266 | 266 | 0 | 0.1 | 0 | 242 | 241 | 244 | 241 | 240 | 243 | 240 | 131 | 7 | 2.2 | 3.4 | 5.5 | 0.5 | 0.8 | 1.2 | 0 | 0.1 | 0.1 | 0.5 | 0.9 | 1.1 | 8 | 12 | 18 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.4 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 100 | 90 | 50 | 90 | all equitment in good conditions | ABDUL AZIN | 11727 | AZHAR YUNUS | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_11.pdf | RAN | 20/07/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 37.7 | 43.7 | 220 |  |  | 266 | 266 | 0 | 0 | 0 | 243 | 243 | 245 | 244 | 243 | 246 | 240 | 240 | 240 | 2.2 | 3.9 | 5.5 | 0.5 | 0.9 | 1.2 | 0 | 0.2 | 0.1 | 0.5 | 0.9 | 1.3 | 7 | 15 | 19 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Battery in good condition and all cable at bank properly connected |  | 20160 |  | 7223 | KLMFEP-33001
4000555093 | SC_PM_QTR_UPS_4000555093.pdf | RAN | 20/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.8 | 39.0 | 229 | 50 | 50 | 267 | 267 | 0 | 0.1 | 0 | 242 | 241 | 242 | 241 | 240 | 242 | 239 | 239 | 240 | 2.1 | 3.8 | 5.3 | 0.5 | 0.8 | 1.2 | 0 | 0.1 | 0.1 | 0.5 | 0.8 | 1.3 | 7 | 12 | 19 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [7 empty] | 7222 |  | 7111 | KLMFEP-33001
4000608067 | SC_PM_QTR_UPS_4000608067.pdf | RAN | 20/04/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36.8 | 41.5 | 230 | 50.04 | 50 | 266 | 266 | 0 | 0 | 0 | 242 | 242 | 244 | 243 | 241 | 244 | 240 | 240 | 240 | 1.8 | 3.8 | 5.3 | 0.4 | 0.8 | 1.3 | 0 | 0.2 | 0.1 | 0.4 | 0.9 | 1.2 | 6 | 14 | 19 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Module and battenes in good condition. Bank 2 and 3 don't have batteries Only used Bank 1. |  | 19921 |  | 7111 | KLMFEP-33001
4000530706 | SC_PM_QTR_UPS_4000530706.pdf | RAN | 20/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.4 | 34.6 | 246 | 50 | 50 | 268 | 268 | 0 | 0 | 0 | 234 | 234 | 240 | 236 | 238 | 236 | 240 | 240 | 240 | 1.6 | 4.5 | 3.7 | 0.4 | 1 | 0.8 | 0 | 0.2 | 0.1 | 0.3 | 1.1 | 0.8 | 5 | 15 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.2 | 12.8 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 200 | 100 | 100 | 50 | 100 | all equipment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
4000467101 | SC_PM_QTR_UPS_4000467101.pdf | RAN | 20/04/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 49.5 | 32.5 | 150 | 50 | 50 | 298 | 282 | 0 | 0 | 0 | 246 | 247 | 249 | 282 | 281 | 283 | 244 | 242 | 241 | 0.1 | 0.1 | 0.2 | 1 | 1.1 | 1.2 | 0.1 | 0.2 | 0.5 | 0.4 | 0.7 | 0.6 | 8 | 16 | 23 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.8 | 15.2 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 120 | 100 | 80 | 50 | 80 | ok |  | 7110 |  | 7111 | KLMFEP-33001
4000668095 | SC_PM_QTR_UPS_4000668095.pdf | RAN | 20/01/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36.8 | 43.0 | 237 |  |  | 266 | 266 | 0 | 0 | 0 | 241 | 240 | 243 | 241 | 240 | 243 | 240 | 240 | 240 | 2 | 4.1 | 4.9 | 0.5 | 0.9 | 1.2 | 0 | 0.3 | 0.1 | 0.5 | 1 | 1.2 | 7 | 13 | 17 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Only one bank (Bank A and Bank B) Other that, all equipment in a good conditions. |  | 22777 |  | 7222 | KLMFEP-33001
4000597864 | SC_PM_QTR_UPS_4000597864.pdf | RAN | 20/01/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.1 | 37.1 | 230 | 50.08 | 50 | 266 | 266 | 0 | 0 | 0 | 243 | 242 | 245 | 242 | 242 | 245 | 240 | 239 | 240 | 2 | 3.7 | 5.3 | 0.4 | 0.9 | 1.2 | 0 | 0.1 | 0.1 | 0.5 | 1 | 1.2 | 7 | 13 | 18 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | - Battery Bank 3 (EO1 - F40) need to be replaced - Battery 3 value is below 12V (EO1 - F40) |  | 20079 |  | 7111 | KLMFEP-33001
4000509057 | SC_PM_QTR_UPS_4000509057.pdf | RAN | 20/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 32.7 | 39.0 | 208.8 | 50 | 50 | 266 | 266 | 0 | 0.1 | 0.1 | 242 | 241 | 242 | 241 | 240 | 242 | 239 | 239 | 240 | 211 | 3.8 | 5.3 | 0.5 | 0.8 | 1.2 | 0 | 0.1 | 0.2 | 0.5 | 0.8 | 1.2 | 7 | 12 | 19 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.1 | 12.9 | 12.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 90 |  |  | 7222 |  | 7111 | KLMFEP-33001
4000446322 | SC_PM_QTR_UPS_4000446322.pdf | RAN | 20/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 48.5 | 32.5 | 150 | 50 | 50 | 282 | 253 | 0 | 0 | 0 | 246 | 247 | 249 | 282 | 281 | 283 | 244 | 242 | 241 | 0.1 | 0.1 | 0.2 | 1 | 1.1 | 1.2 | 0.1 | 0.2 | 0.5 | 0.4 | 0.7 | 0.6 | 8 | 1.6 | 2.3 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.8 | 13.2 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 100 | 50 | 50 | 80 | ok |  | 7223 |  | 7111 | KLMFEP-33001
4000646740 | SC_PM_QTR_UPS_4000646740.pdf | BNG | 19/10/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.3 | 34.2 | 268.8 | 50.02 | 50 | 266 | 266 | 0 | 0 | 0 | 245 | 243 | 246 | 245 | 245 | 246 | 240 | 239 | 240 | 2.7 | 6.1 | 3.9 | 0.6 | 1.4 | 0.9 | 0.1 | 0 | 0 | 0.6 | 1.5 | 0.8 | 10 | 22 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipments in a good condition. |  | 22547 |  | 7262 | KLMFEP-33001
4000576113 | SC_PM_QTR_UPS_4000576113.pdf | BNG | 19/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 40.3 | 43.7 | 50 | 50 | 50 | 266 | 266 | 0 | 0 | 0 | 252 | 249 | 252 | 251 | 250 | 253 | 240 | 239 | 240 | 3 | 6.4 | 3.7 | 0.7 | 1.4 | 0.8 | 0.1 | 0.2 | 0.1 | 0.7 | 1.4 | 0.9 | 10 | 23 | 13 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.4 | 13.2 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 50 | 100 | 49 | 48 | 49 | All in good condition |  | 19898 |  | 7111 | KLMFEP-33001
4000493756 | SC_PM_QTR_UPS_4000493756.pdf | BNG | 19/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.2 | 36.4 | 228 |  |  | 260 | 266 | 0 | 0 | 0 | 230 | 249 | 253 | 249 | 249 | 254 | 239 | 239 | 240 | 2.7 | 3.1 | 3.8 | 0.6 | 1.4 | 0.9 | 0 | 0.2 | 0 | 5.6 | 1.4 | 1.8 | 9 | 22 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.6 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 150 | 100 | 70 | 50 | 70 | Good Condition. |  | 7223 |  | 7111 | KLMFEP-33001
4000480668 | SC_PM_QTR_UPS_4000480668.pdf | BNG | 2022-07-19 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 32.4 | 36.4 | 48 | 50 | 50 | 260 | 264 | 0 | 0 | 0 | 250 | 249 | 253 | 249 | 244 | 253 | 239 | 239 | 240 | 2.7 | 3.1 | 3.8 | 0.6 | 1.4 | 0.9 | 0 | 0.2 | 0 | 0.6 | 1.4 | 1.8 | 9 | 22 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.1 | 13.6 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 150 | 100 | 70 | 50 | 70 | all equitment in good condition | ABDUL AZIN | 11727 | AZHAR YUNUS | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_8.pdf | BNG | 19/07/2024 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 31.6 | 33.1 | 591 |  |  | 266 | 266 | 0 | 0 | 0 | 245 | 244 | 247 | [6 empty] | 2.7 | 6.4 | 3.4 | 0.6 | 1.5 | 0.8 | 0.1 | 0 | 0 | 0.6 | 1.5 | 1.9 | 10 | 23 | 13 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | all ementien in good condition |  | 20159 |  | 7256 | KLMFEP-33001
4000555042 | SC_PM_QTR_UPS_4000555042.pdf | BNG | 19/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 46.0 | 50.9 | 54 | 50 | 50 | 266 | 264 | 0 | 0 | 0 | 246 | 243 | 246 | 245 | 239 | 240 | 240 | 239 | 240 | 2.7 | 5.5 | 3.5 | 0.6 | 1.2 | 0.6 | 0.1 | 0.2 | 0.1 | 0.6 | 1.2 | 0.8 | 12 |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | An equipment in good conditions |  | 7256 |  | 7111 | KLMFEP-33001
4000608017 | SC_PM_QTR_UPS_4000608017.pdf | BNG | 19/04/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.4 | 36.5 | 616.2 | 50 | 50 | 266 | 267 | 0 | 0 | 0 | 243 | 242 | 245 | 244 | 242 | 246 | 240 | 240 | 239 | 2.7 | 6.5 | 3.9 | 0.6 | 0.5 | 0.7 | 0 | 0.1 | 0 | 0.6 | 0.4 | 1.7 | 9 | 22 | 12 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | ADC change 2 module UPS. Bank 3 dosnt have batteries. Module and all batteries in good condition. |  | 19921 |  | 7111 | KLMFEP-33001
4000530667 | SC_PM_QTR_UPS_4000530667.pdf | BNG | 19/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 46.0 | 50.9 | 54 |  |  | 266 | 266 | 0 | 0 | 0 | 246 | 243 | 246 | 245 | 243 | 247 | 240 | 239 | 240 | 2.7 | 5.5 | 3.5 | 0.6 | 1.2 | 0.7 | 0.1 | 0.2 | 0.1 | 0.6 | 1.2 | 0.8 | 10 | 101 | 12 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.4 | 12.8 | 13.9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 55 | 100 | 25 | 50 | 55 | all equipment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
4000467069 | SC_PM_QTR_UPS_4000467069.pdf | BNG | 19/04/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 220 | 50 | 50 | 270 | 270 | 0 | 0 | 0 | 249 | 246 | 249 | 248 | 247 | 230 | 239 | 239 | 240 | 2.7 | 4.8 | 3.9 | 0.6 | 0.6 | 1 | 0 | 0.1 | 0 | 0.6 | 1.1 | 1 | 10 | 16 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.7 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 100 | 50 | 50 | 90 | 2 battery bank faulty |  | 7110 |  | 7111 | KLMFEP-33001
4000660374 | SC_PM_QTR_UPS_4000660374.pdf | BNG | 19/01/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.2 | 31.9 | 606 | 50 | 50 | 266 | 266 | 0 | 0 | 0 | 249 | 247 | 251 | 249 | 247 | 251 | 240 | 239 | 240 | 2.8 | 6.2 | 3.6 | 0.6 | 1.4 | 1 | 0.2 | 0.1 | 0.1 | 0.6 | 1.4 | 0.8 | 10 | 22 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipment in a good condition. |  | 22775 |  | 7110 | KLMFEP-33001
4000597708 | SC_PM_QTR_UPS_4000597708.pdf | BNG | 19/01/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 32.8 | 35.7 | 53 |  |  | 266 | 266 | 0 | 0 | 0 | 248 | 246 | 250 | 247 | 246 | 250 | 239 | 239 | 240 | 3 | 6.6 | 4 | 0.7 | 1.6 | 0.9 | 0 | 0.2 | 0 | 0.7 | 1.6 | 1 | 11 | 24 | 15 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Module need to calibrate. All battery in good condition. |  | 20452 |  | 7111 | KLMFEP-33001
4000509121 | SC_PM_QTR_UPS_4000509121.pdf | BNG | 19/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.1 | 36.4 | 220 | 50 | 50 | 260 | 266 | 0 | 0 | 0 | 230 | 249 | 253 | 249 | 249 | 254 | 239 | 239 | 240 | 2.7 | 3.1 | 3.8 | 0.6 | 1.4 | 0.9 | 0 | 0.2 | 0 | 0.6 | 1.4 | 1.8 | 9 | 22 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.4 | 13.2 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 150 | 100 | 75 | 50 | 75 |  |  | 7222 |  | 7111 | KLMFEP-33001
4000446363 | SC_PM_QTR_UPS_4000446363.pdf | BNG | 19/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 45.8 | 50.7 | 220 |  |  | 270 | 270 | 0 | 0 | 0 | 249 | 296 | 249 | 248 | 247 | 280 | 239 | 239 | 240 | 2.7 | 4.8 | 3.9 | 0.6 | 0.6 | 1 | 0 | 0.1 | 0 | 0.6 | 1.1 | 1 | 10 | 16 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.7 | 12.8 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 80 | 100 | 40 | 50 | 40 | 2 battery book faulty |  | 7222 |  | 7111 | KLMFEP-33001
4000644023 | SC_PM_QTR_UPS_4000644023.pdf | IBI | 18/10/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36.0 | 42.7 | 123 |  |  | 266 | 266 | 0 | 0 | 0 | 245 | 245 | 248 | 245 | 245 | 247 | 239 | 239 | 239 | 2.9 | 7.1 | 10.4 | 0.6 | 1.4 | 2.4 | 0 | 0.5 | 0.5 | 0.6 | 1.6 | 2.5 | 10 | 25 | 38 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipments in a good condition. |  | 22547 |  | 7262 | KLMFEP-33001
4000576144 | SC_PM_QTR_UPS_4000576144.pdf | IBI | 18/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 30 | 35.4 | 120 | 50.02 | 50 | 233 | 273 | 0 | 0 | 0 | 252 | 252 | 256 | 252 | 252 | 254 | 239 | 239 | 239 | 2.9 | 6.7 | 11.3 | 0.7 | 1.3 | 2.6 | 0 | 0.5 | 0.5 | 0.6 | 1.7 | 2.7 | 22 | 32 | 40 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.3 | 13.4 | [25 empty] | Slave module faulty only use 1 bank batteries |  | 19898 |  | 7111 | KLMFEP-33001
4000493774 | SC_PM_QTR_UPS_4000493774.pdf | IBI | 18/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36 |  | 138 | 50 | 50 | 236 | 236 | 0 | 0 | 0 | 250 | 250 | 251 | 250 | 250 | 252 | 239 | 239 | 240 | 3.2 | 6.9 | 7.7 | 0.7 | 1.5 | 2 | 0.1 | 0.4 | 0.2 | 0.7 | 1.6 | 1.9 | 11 | 23 | 29 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.8 | 12.9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 186 | 100 | 80 | 50 |  |  |  | 7222 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_5.pdf | IBI | 18/07/2024 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 40.7 | 48.1 | 111 |  |  | 266 | 266 | 0 | 0 | 0 | 242 | 242 | 245 | 242 | 242 | 244 |  |  |  | 2.9 | 7 | 10.7 | 0.6 | 1.4 | 2.6 | 0 | 0.5 | 0.5 | 0.6 | 1.7 | 2.6 | 10 | 27 | 39 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | UPS in good condition. |  | 20159 |  | 7256 | KLMFEP-33001
4000555072 | SC_PM_QTR_UPS_4000555072.pdf | IBI | 18/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 46.0 | 50.9 | 54 |  |  | 266 | 266 | 0 | 0 | 0 | 246 | 243 | 246 | 245 | 243 | 247 | 240 | 239 | 240 | 2.7 | 5.5 | 3.5 | 0.6 | 1.2 | 0.7 | 0.1 | 0.2 | 0.1 | 0.6 | 1.2 | 0.8 | 10 | 19 | 12 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | all equipment in good condition. |  | 7256 |  | 7111 | KLMFEP-33001
4000480689 | SC_PM_QTR_UPS_4000480689.pdf | IBI | 18/07/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36 |  | 129 | 50 | 50 | 286 | 286 | 0 | 0 | 0 | 250 | 250 | 254 | 250 | 250 | 252 | 239 | 239 | 240 | 3.2 | 6.9 | 7.7 | 0.7 | 1.5 | 2 | 0 | 0.4 | 0.2 | 0.7 | 1.6 | 1.9 | 11 | 23 | 29 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.8 | 12.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 190 | 100 | 80 | 50 | 80 | ok | ROHIZAN | 7223 | AZHAR YUNUS | 7111 | KLMFEP-33001
4000608042 | SC_PM_QTR_UPS_4000608042.pdf | IBI | 18/04/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 120 | 50.04 | 50 | 269 | 269 | 0 | 0 | 0 | 251 | 251 | 255 | 251 | 251 | 252 | 240 | 239 | 239 | 2.9 | 6.5 | 10.8 | 0.7 | 1.4 | 2.6 | 0 | 0.5 | 0.4 | 0.7 | 1.6 | 2.5 | 11 | 23 | 38 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Equipment is in good condition. Battery bank 2 no batery (C and D) |  | 20449 |  | 7111 | KLMFEP-33001
4000530683 | SC_PM_QTR_UPS_4000530683.pdf | IBI | 18/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 37.7 | 44.7 | 122 |  |  | 268 | 268 | 0 | 0 | 0 | 252 | 253 | 256 | 253 | 253 | 254 | 239 | 239 | 239 | 2.7 | 6.2 | 11.4 | 0.6 | 1.4 | 2.6 | 0 | 0.5 | 0.5 | 0.6 | 1.4 | 2.7 | 9 | 22 | 41 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.2 | 12.8 | 13 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 150 | 100 | 100 | 50 | 180 | all equitment in good conditions #1 unit bateri bank not good condition 1 unit module faulty |  | 11727 |  | 7111 | KLMFEP-33001
4000467087 | SC_PM_QTR_UPS_4000467087.pdf | IBI | 18/04/2022 |  | TRUE | TRUE | 1 unit module faults (share module) | TRUE | TRUE | 100 | 36.4 | 44.4 | 137 |  |  | 206 | 286 | 0 | 0 | 0 | 250 | 250 | 254 | 250 | 250 | 254 | 239 | 259 | 239 | 3.2 | 6.9 | 7.4 | 0.7 | 1.5 | 2 | 0 | 0.4 | 0.2 | 0.7 | 1.6 | 1.9 | 11 | 23 | 29 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.4 | 12.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 150 | 100 | 80 | 50 | 150 | OK |  | 7110 |  | 7111 | KLMFEP-33001
4000669108 | SC_PM_QTR_UPS_4000669108.pdf | IBI | 18/01/2025 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 31.5 | 35.2 | 121.8 |  |  | 266 | 266 | 0 | 0 | 0 | 243 | 243 | 246 | 243 | 243 | 245 | 240 | 240 | 239 | 2.9 | 6.8 | 4.7 | 0.6 | 1.5 | 2.5 | 0 | 0.6 | 0.5 | 0.7 | 1.7 | 2.5 | 10 | 25 | 36 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipment in a good condition |  | 22775 |  | 7110 | KLMFEP-33001
4000597779 | SC_PM_QTR_UPS_4000597779.pdf | IBI | 18/01/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 31.5 | 38.1 | 120 |  |  | 268 | 268 | 0 | 0 | 0 | 245 | 246 | 249 | 245 | 246 | 248 | 239 | 239 | 240 | 3.2 | 6.5 | 10.7 | 0.7 | 1.4 | 2.5 | 0 | 0.5 | 0.5 | 0.7 | 1.6 | 2.5 | 11 | 23 | 38 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | -Module P2 notified alarm Phase Fault -there are serval Faulty battery burn -beside that hardware in good condition - Bank 1 and 2 kembung |  | 20079 |  | 7111 | KLMFEP-33001
4000509107 | SC_PM_QTR_UPS_4000509107.pdf | IBI | 18/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36 |  | 190 | 60 | 50 | 286 | 286 | 0 | 0 | 0 | 250 | 250 | 254 | 250 | 250 | 254 | 239 | 239 | 240 | 3.2 | 6.4 | 7.1 | 0.4 | 1.5 | 2 | 0 | 0.4 | 0.2 | 0.7 | 1.6 | 1.9 | 11 | 24 | 30 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.8 | 12.9 | 12.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 140 | 100 | 95 | 50 | 95 | All equipment in good condition. | YARUL AZWAN | 7110 |  |  | KLMFEP-33001
4000446346 | SC_PM_QTR_UPS_4000446346.pdf | IBI | 18/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36.4 | 44.4 | 137 |  |  | 286 | 286 | 0 | 0 | 0 | 280 | 250 | 254 | 280 | 250 | 254 | 239 | 239 | 239 | 3.2 | 6.9 | 7.7 | 0.7 | 1.5 | 2 | 0 | 0.4 | 0.2 | 0.7 | 1.6 | 1.9 | 11 | 23 | 29 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.8 | 12.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 160 | 100 | 80 | 50 | 80 | ok |  | 7222 |  | 7111 | KLMFEP-33001
4000576134 | SC_PM_QTR_UPS_4000576134.pdf | HAH | 17/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.3 | 38.8 | 233 | 50.5 | 50 | 267 | 267 | 0.1 | 0.1 | 0 | 238 | 238 | 240 | 236 | 237 | 240 | 239 | 239 | 246 | 1.5 | 6.3 | 3.4 | 0.4 | 1.4 | 0.7 | 1 | 0.1 | 0.1 | 0.4 | 1.4 | 0.7 | 6 | 22 | 10 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | all equipment in good conditiong |  | 7256 |  | 7111 | KLMFEP-33001
4000493769 | SC_PM_QTR_UPS_4000493769.pdf | HAH | 17/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36 |  | 372 | 50 | 50 | 271 | 271 | 0 | 0 | 0 | 237 | 236 | 239 | 238 | 236 | 239 | 239 | 239 | 240 | 1.4 | 2.3 | 2.7 | 0.3 | 0.5 | 0.6 | 0 | 0 | 0.1 | 0.3 | 0.5 | 0.6 | 5 | 8 | 9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.5 | 12.6 | 12.5 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 90 |  |  | 7222 |  | 7111 | KLMFEP-33001
4000646788 | SC_PM_QTR_UPS_4000646788.pdf | HAH | 17/10/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 321 |  |  | 267 | 267 | 0 | 0 | 0 | 240 | 239 | 242 | 239 | 238 | 242 | 239 | 240 | 240 | 1.5 | 3.6 | 2.9 | 0.3 | 0.8 | 0.6 | 10 | 0 | 0.1 | 0.3 | 0.8 | 0.6 | 5 | 12 | 9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipment in a good condition. |  | 20858 |  | 7262 | KLMFEP-33001
| SC_PM_NA_UPS_NA_6.pdf | HAH | 17/07/7024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 37.1 | 42.9 | 315 |  |  | 267 | 267 | 0 | 0.1 | 0 | 241 | 239 | 242 | 241 | 239 | 241 |  |  |  | 1.6 | 3.5 | 3.4 | 0.4 | 0.8 | 0.7 | 0 | 0 | 0 | 0.3 | 0.8 | 0.7 | 5 | 13 | 10 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipment in good condition. |  | 19920 |  | 7256 | KLMFEP-33001
4000555066 | SC_PM_QTR_UPS_4000555066.pdf | HAH | 17/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.9 | 39.9 | 280 |  |  | 267 | 267 | 0.1 | 0.1 | 0 | 237 | 236 | 239 | 238 | 236 | 239 | 239 | 239 | 240 | 1.6 | 3.6 | 2.8 | 0.3 | 0.7 | 0.8 | 0 | 0 | 0 | 0.3 | 0.8 | 0.8 | 5 | 13 | 12 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | all equipment in good condition |  | 7256 |  | 7111 | KLMFEP-33001
4000480684 | SC_PM_QTR_UPS_4000480684.pdf | HAH | 17/07/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36 |  | 380 |  |  | 271 | 271 | 0 | 0 | 0 | 237 | 236 | 239 | 237 | 236 | 239 | 238 | 239 | 239 | 1.4 | 2.3 | 2.7 | 0.3 | 0.5 | 0.6 | 0 | 0 | 0.1 | 0.3 | 0.5 | 0.6 | 8 | 8 | 9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.5 | 12.6 | 12.8 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 170 | 100 | 90 | 50 | 90 |  | ROHIZAN | 7223 | AZHAR YUNUS | 7111 | KLMFEP-33001
4000608037 | SC_PM_QTR_UPS_4000608037.pdf | HAH | 17/04/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 254 | 50.5 | 50 | 267 | 267 | 0.1 | 0.1 | 0 | 239 | 237 | 240 | 238 | 237 | 240 | 239 | 239 | 240 | 1.6 | 3.5 | 3.7 | 0.4 | 0.8 | 0.7 | 0 | 0 | 0 | 0.3 | 0.9 | 0.7 | 5 | 12 | 11 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Bank 1 & Bank 2 dismantle further maintenance |  | 20449 |  | 7111 | KLMFEP-33001
4000530679 | SC_PM_QTR_UPS_4000530679.pdf | HAH | 17/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36.9 | 43.0 | 240 |  |  | 267 | 267 | 0 | 0.1 | 0 | 239 | 237 | 239 | 238 | 237 | 240 | 239 | 240 | 240 | 1.6 | 6.1 | 2.6 | 0.4 | 1.3 | 0.7 | 0 | 0 | 0.1 | 0.4 | 1.4 | 0.6 | 5 | 21 | 9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.8 | 13.2 | 13.1 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 150 | 100 | 150 | 50 | 180 | all equipment |  | 11727 |  | 7111 | KLMFEP-33001
4000467082 | SC_PM_QTR_UPS_4000467082.pdf | HAH | 17/04/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 37.9 | 58.9 | 326 | 50.06 | 50 | 271 | 271 | 0 | 0 | 0 | 238 | 237 | 240 | 238 | 237 | 24 | 239 | 239 | 240 | 1.3 | 3.8 | 2.6 | 0.3 | 0.8 | 0.6 | 0 | 0 | 0.1 | 0.3 | 0.9 | 0.6 | 4 | 15 | 9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.4 | 13.4 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 150 | 100 | 80 | 50 | 80 | all equitment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
4000669114 | SC_PM_QTR_UPS_4000669114.pdf | HAH | 17/01/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 30.8 | 34.7 | 273 |  |  | 26.7 | 26.7 | 0 | 0 | 0 | 235 | 234 | 236 | 235 | 234 | 239 | 239 | 240 | 240 | 1.4 | 3.8 | 2.6 | 0.3 | 0.8 | 0.6 | 0 | 0.1 | 0.1 | 0.3 | 0.9 | 0.6 | 5 | 13 | 10 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All battery and module working properly without any error. Bank 1 and 2 not available. Only bank 3 is available and in good condition |  | 22775 |  | 7110 | KLMFEP-33001
4000597748 | SC_PM_QTR_UPS_4000597748.pdf | HAH | 17/01/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 35.7 | 41.5 | 330 | 50.04 | 50 | 267 | 267 | 0.1 | 0.1 | 0 | 240 | 237 | 240 | 238 | 237 | 240 | 240 | 239 | 240 | 1.5 | 3.5 | 3 | 0.3 | 0.8 | 0.7 | 0 | 0 | 0 | 0.3 | 0.8 | 0.7 | 5 | 13 | 10 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | * all battery fault except bank F. * condition both module in good condition. * battery take out. except bank F |  | 19898 |  | 7111 | KLMFEP-33001
4000509110 | SC_PM_QTR_UPS_4000509110.pdf | HAH | 17/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 24 |  | 126 | 50 | 50 | 277 | 271 | 0 | 0 | 0 | 255 | 254 | 256 | 255 | 254 | 256 | 239 | 239 | 239 | 3.2 | 6.3 | 7.6 | 0.7 | 1.5 | 1.8 | 0 | 0.3 | 0.5 | 0.7 | 1.6 | 1.8 | 11 | 19 | 20 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.5 | 12.6 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 160 | 100 | 80 | 50 | 60 | All annection cable with battery in secure procution. |  | 1110 |  | 7111 | KLMFEP-33001
4000446351 | SC_PM_QTR_UPS_4000446351.pdf | HAH | 17/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36.6 | 49.4 | 332 |  | 50 | 271 | 271 | 0 | 0 | 0 | 247 | 247 | 239 | 248 | 276 | 239 | 239 | 239 | 239 | 1.11 | 2.3 | 2.7 | 0.3 | 0.5 | 0.6 | 0 | 0 | 0.1 | 0.3 | 0.5 | 0.6 | 5 | 8 | 9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.6 | 12.8 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 160 | 100 | 80 | 50 | 150 | All equipment in good condition |  | 7222 |  | 7111 | KLMFEP-33001
4000576156 | SC_PM_QTR_UPS_4000576156.pdf | MAH | 16/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 34.7 | 41.6 | 122 |  |  | 267 | 267 | 0 | 0 | 0 | 243 | 242 | 243 | 243 | 243 | 244 | 239 | 239 | 239 | 3.4 | 6.2 | 10.4 | 0.7 | 1.3 | 2.2 | 0 | 0.3 | 0.7 | 0.8 | 1.7 | 2.5 | 11 | 23 | 37 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All good condition |  | 19920 |  | 7111 | KLMFEP-33001
4000493791 | SC_PM_QTR_UPS_4000493791.pdf | MAH | 16/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 34 |  | 136 | 50 | 50 | 271 | 271 | 0 | 0.7 | 0 | 255 | 254 | 253 | 255 | 256 | 256 | 239 | 239 | 239 | 3.2 | 6.3 | 7.6 | 0.7 | 1.5 | 1.8 | 0 | 0.3 | 0.5 | 0.7 | 1.5 | 0.8 | 11 | 23 | 27 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.5 | 12.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 160 | 100 | 80 | 50 | 60 |  |  | 7222 |  | 7111 | KLMFEP-33001
4000646818 | SC_PM_QTR_UPS_4000646818.pdf | MAH | 16/10/2024 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 36 | 40.9 | 128 | 50 | 50 | 267 | 267 | 0 | 0 | 0 | 243 | 241 | 246 | 243 | 242 | 245 | 239 | 239 | 239 | 3.6 | 7.6 | 9.6 | 0.8 | 1.6 | 2.2 | 0.1 | 0.4 | 0.6 | 0.4 | 1.6 | 2.2 | 12 | 23 | 34 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipment in good condition |  | 22547 |  | 7202 | KLMFEP-33001
| SC_PM_NA_UPS_NA_13.pdf | MAH | 16/07/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 35.2 | 42 | 126 | 50.04 | 50 | 267 | 267 | 0 | 0.1 | 0 | 248 | 247 | 249 | 248 | 248 | 250 | 239 | 239 | 239 | 36 | 6 | 9 | 0.8 | 1.5 | 2 | 0.1 | 0.3 | 0.5 | 0.4 | 1.5 | 2.2 | 13 | 23 | 34 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipment in good condition |  | 9920 |  | 7256 | KLMFEP-33001
4000541165 | SC_PM_QTR_UPS_4000541165.pdf | MAH | 16/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 65 |  | 100 | 50 | 80 | 267 | 207 | 0 | 0.1 | 0 | 245 | 245 | 247 | 246 | 246 | 246 | 239 | 239 | 241 | 5.2 | 5.6 | 10.4 | 0.8 | 1.4 | 2.3 | 0 | 0.3 | 0.6 | 0.8 | 1.4 | 2.4 | 12 | 25 | 38 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | one module operated |  | 7223 |  | 7111 | KLMFEP-33001
4000480697 | SC_PM_QTR_UPS_4000480697.pdf | MAH | 16/07/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 30 |  | 129.6 | 50 | 50 | 271 | 271 | 0 | 0.7 | 0 | 255 | 254 | 256 | 255 | 256 | 256 | 239 | 237 | 239 | 3.2 | 6.3 | 7.6 | 0.7 | 15 | 1.8 | 0 | 0.3 | 0.5 | 0.7 | 1.5 | 0.8 | 11 | 23 | 27 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.8 | 12.6 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 160 | 100 | 80 | 50 | 60 | OK | ROHIZAN | 7223 | AZHAR YUNUS | 7111 | KLMFEP-33001
4000608051 | SC_PM_QTR_UPS_4000608051.pdf | MAH | 16/04/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 133 | 50 | 50 | 267 | 267 | 0.1 | 0.1 | 0 | 247 | 246 | 248 | 248 | 248 | 249 | 239 | 239 | 239 | 2.7 | 7.1 | 9.6 | 0.9 | 1.5 | 2.2 | 0 | 0.3 | 0.6 | 0.6 | 1.5 | 2.3 | 9 | 22 | 35 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Bank 1 TRANSFER to HanG TUAH. Module 1 Problem.Equipment in good condition |  | 20449 |  | 7011 | KLMFEP-33001
4000530695 | SC_PM_QTR_UPS_4000530695.pdf | MAH | 16/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 35.8 |  | 120 | 50 | 50 | 267 | 267 | 0 | 0 | 0 | 245 | 244 | 246 | 245 | 245 | 245 | 239 | 240 | 239 | 2.7 | 6.7 | 9.6 | 0.6 | 1.5 | 2.2 | 0 | 0.3 | 0.5 | 0.6 | 1.6 | 2.3 | 10 | 23 | 37 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.3 | 12.2 | 12.5 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 120 | 100 | 60 | 50 | 60 |  |  | 7223 |  | 7111 | KLMFEP-33001
4000467093 | SC_PM_QTR_UPS_4000467093.pdf | MAH | 16/04/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 32.2 | 38.9 | 133 | 50.01 | 50 | 271 | 271 | 0 | 0 | 0 | 248 | 248 | 248 | 248 | 249 | 249 | 239 | 239 | 240 | 2 |  | 6.9 | 0.4 | 1.4 | 2.4 | 0 | 0.2 | 0.8 | 0.5 | 1.4 | 2.6 | 7 | 23 | 37 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.6 | 13.6 | 13.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 60 | 50 | 60 | all equipment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
4000467110 | SC_PM_QTR_UPS_4000467110.pdf | TUN | 16/04/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 24.7 | 22.6 | 122 | 49.9 | 49.6 | 267 | 267 | 768.3 | 268.1 | 1.3 |  |  |  | 244 | 243 | 243 | 241 | 241 | 241 | 0.2 | 2.1 | 1.5 | 0.4 | 1.9 | 2.4 | 0 | 0.2 | 0.5 | 0.5 | 1.4 | 2.6 | 7 | 23 | 36 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.4 | 13.4 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 110 | 100 | 60 | 50 | 105 | all equipment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
4000668132 | SC_PM_QTR_UPS_4000668132.pdf | MAH | 16/01/2025 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 36.3 | 42.8 | 125 |  |  | 267 | 267 | 0 | 0.1 | 0 | 244 | 243 | 246 | 244 | 244 | 247 | 239 | 239 | 239 | 2.7 | 6.7 | 9.6 | 0.8 | 0.7 | 2.3 | 0.1 | 0.5 | 0.5 | 0.8 | 2.6 | 2.2 | 12 | 23 | 34 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | Bank A not available, All battery in good condition. |  | 22775 |  | 7110 | KLMFEP-33001
4000597813 | SC_PM_QTR_UPS_4000597813.pdf | MAH | 16/01/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 39.0 | 45.8 | 122 | 50 | 50 | 267 | 267 | 0 | 0.1 | 0 | 246 | 246 | 247 | 247 | 247 | 248 | 239 | 239 | 239 | 3.3 | 6.3 | 9.5 | 0.8 | 1.6 | 2.3 | 0 | 0.2 | 0.6 | 0.8 | 1.5 | 2.3 | 12 | 22 | 35 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [11 empty] | 1. Only used 1 module because module power failure (module 1) 2. All batteries in good condition 3. Equipment in good condition. |  | 20826 |  | 7111 | KLMFEP-33001
4000509102 | SC_PM_QTR_UPS_4000509102.pdf | MAH | 16/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 30 |  | 136 | 50 | 50 | 271 | 271 | 0 | 0.7 |  | 255 | 254 | 236 | 255 | 256 | 256 | 239 | 239 | 239 | 2.2 | 6.3 | 7.6 | 0.7 | 1.5 | 1.3 | 0 | 0.3 | 0.5 | 0.7 | 1.5 | 1.8 | 11 | 23 | 27 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.4 | 13.2 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 160 | 100 | 80 | 80 | 60 | An eaupment modem and battery in good artition. |  | 7110 |  | 7111 | KLMFEP-33001
4000446338 | SC_PM_QTR_UPS_4000446338.pdf | MAH | 16/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 34.1 | 41.5 | 196 | 80 |  | 271 | 271 | 0 | 0 | 0 | 255 | 256 | 254 | 255 | 256 | 254 | 229 | 239 | 239 | 3.2 | 6.1 | 7.6 | 0.7 | 1.6 | 1.8 | 0 | 0.3 | 0.5 | 0.7 | 1.5 | 1.8 | 11 | 23 | 27 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.8 | 12.6 | 12.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 240 | 100 | 120 | 50 | 120 | ok |  | 7222 |  | 7111 | KLMFEP-33001
4000647425 | SC_PM_QTR_UPS_4000647425.pdf | Tun | 15/10/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 21 | 23 |  | 50 | 50 | 267 | 267 | 267 | 268 | 0 | 55 | 1 | 34 | 242 | 240 | 243 | 241 | 241 | 241 | 0.2 | 2.2 | 1.8 | 0.1 | 0.4 | 0.3 | 0.4 | 2 | 1.6 | 0.3 | 1 | 1 | 84.4 | 16.3 | 15.9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All in good condition |  | 19922 |  | 7248 | KLMFEP-33001
4000576195 | SC_PM_QTR_UPS_4000576195.pdf | Tun | 15/10/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  |  | 50 |  | 261 | 261 | 0 | 0 |  |  |  |  | 243 | 242 | 244 | 241 | 241 | 241 | 1 | 8.1 | 6.5 | 0.2 | 1.6 | 1.1 | 0.1 | 2 | 1.6 | 0 | 0.8 | 1 | 0.8 | 0.84 | 0.75 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.2 | 13.4 | 13.5 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 186 | 100 | 68 | 50 | 60 | good condition |  | 7248 |  | 7111 | KLMFEP-33001
4000509049 | SC_PM_QTR_UPS_4000509049.pdf | TUN | 15/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33 |  | 180 |  |  | 241 | 242 | 0.2 | 0.1 | 1.9 | 243 | 244 | 245 | 244 | 243 | 244 | 241 | 240 | 244 | 1.9 | 6.5 | 6.4 | 0.2 | 0.1 | 0.1 | 0.3 | 1.6 | 1.7 | 0.1 | 1.1 | 1.1 | 3.5 | 3.2 | 3 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.3 | 12.5 | 12.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 90 |  |  | 7222 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_4.pdf | TUN | 15/07/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 21.5 |  |  |  |  | 267.7 | 267.7 | 268.2 |  | 0 | 55 | 1 | 34 | 245.3 | 243.5 | 246.8 | 241.5 | 241.3 | 241.3 | 1.8 | 8 | 6.9 | 0.2 | 1.7 | 1.2 | 0.4 | 2 | 1.6 | 0.7 | 1 | 1 | 84.4 | 16.3 | 15.9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All in good condition |  | 20450 |  | 7262 | KLMFEP-33001
4000541175 | SC_PM_QTR_UPS_4000541175.pdf | TUN | 15/07/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  |  | 50 | 50 | 247 | 267 | 0 | 0 |  |  |  |  | 243 | 242 | 244 | 241 | 241 | 241 | 1.6 | 8.1 | 6.5 | 0.2 | 1.6 | 1.1 | 0.4 | 2 | 1.6 | 0 | 0.8 | 1.6 | 0.8 | 0.84 | 0.75 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | good condition. |  | 7223 |  | 7111 | KLMFEP-33001
4000480722 | SC_PM_QTR_UPS_4000480722.pdf | TUN | 15/07/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33 |  | 180 | 50 | 50 | 241 | 242 | 0.2 | 0.1 | 1.9 | 243 | 244 | 245 | 244 | 243 | 244 | 241 | 240 | 244 | 1.9 | 6.5 | 6.4 | 0.2 | 0.1 | 1.1 | 0.3 | 1.6 | 1.7 | 0.1 | 1.1 | 1.1 | 3.5 | 3.2 | 3 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.3 | 12.5 | 12 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 90 | ok | ROHIZAN | 7223 | AZHAR YUNUS | 7111 | KLMFEP-33001
4000608083 | SC_PM_QTR_UPS_4000608083.pdf | TUN | 15/04/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 30 |  | 70 | 50 | 50 | 267 | 267 | 0 | 0 | 0 | 55 | 1 | 34 | 244 | 244 | 246 | 241 | 241 | 241 | 1.9 | 8.3 | 6.5 | 0.2 | 1.7 | 1.2 | 0.4 | 2 | 1.6 | 0.3 | 1 | 1 | 8.4 | 16.3 | 15.9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | all equipment are in good condition |  | 20449 |  | 7111 | KLMFEP-33001
4000520523 | SC_PM_QTR_UPS_4000520523.pdf | TUN | 15/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 54 | 49.9 | 49.5 | 249 | 269 | [6 empty] | 240 | 239 | 241 | 241 | 241 | 247 | 1.9 | 8.2 | 6.4 | 0.1 | 0.5 | 0.5 |  |  |  | 0.5 | 0.5 | 0.4 |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.3 | 12.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 300 | 100 | 180 | 60 | 10 |  |  | 7223 |  | 7111 | KLMFEP-33001
4000668027 | SC_PM_QTR_UPS_4000668027.pdf | TUN | 15/01/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 30.2 | 31.3 | 230 |  |  | 267 | 268 | 0 | 0 | 0 | 244 | 243 | 246 | 244 | 244 | 247 | 239 | 239 | 239 | 2.7 | 6.2 | 9.6 | 0.8 | 0.7 | 2.3 | 0.1 | 0.7 | 2.3 | 0.8 | 2.6 | 2.2 | 12 | 23 | 34 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | all equiptment in good conditions |  | 11727 |  | 11727 | KLMFEP-33001
4000597877 | SC_PM_QTR_UPS_4000597877.pdf | TUN | 15/01/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 30 |  | 70 | 50 | 50 | 267 | 267 | 0 | 0 | 0 | 55 | 1 | 34 | 244 | 244 | 246 | 241 | 241 | 241 | 1.9 | 8.3 | 6.5 | 0.2 | 1.7 | 1.2 | 0.4 | 2 | 1.6 | 0.3 | 1 | 1 | 84.4 | 16.3 | 15.9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipment is in good condition |  | 19898 |  | 7111 | KLMFEP-33001
4000509048 | SC_PM_QTR_UPS_4000509048.pdf | TUN | 15/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 24 | 26 | 360 |  |  | 267.6 | 267.8 | 241.2 | 241.3 |  | 240 | 239 | 241 | 240 | 239 | 241 | 241 | 241 | 241 | 1.9 | 7.9 | 6.9 | 0.2 | 1.7 | 1.1 | 0.2 | 1.9 | 1.4 | 0.3 | 1 | 1 | 3.4 | 14.3 | 11.2 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.2 | 13.4 | 13.5 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 186 | 100 | 68 | 50 | 68 | All equipment module and battery in good condition. |  | 7110 |  | 7111 | KLMFEP-33001
4000446286 | SC_PM_QTR_UPS_4000446286.pdf | TUN | 15/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 34 |  | 180 | 50 | 50 | 241 | 242 | 0.2 | 0.1 | 1.9 | 243 | 241 | 245 | 243 | 244 | 244 | 241 | 240 | 244 | 1.9 | 6.5 | 4 | 0.2 | 0.1 | 1.1 | 0.3 | 1.6 | 1.7 | 0.1 | 1.1 | 1.1 | 3.5 | 3.2 | 3 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.2 | 12.5 | 12.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 180 | 100 | 90 | 50 | 90 | ok |  | 7110 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_1 (7).pdf | KLS | 14/10/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 35.2 | 43.6 | 224 | 50 | 50 | 267 | 268 | 0 | 0 | 0 | 256 | 255 | 257 | 255 | 255 | 256 | 239 | 238 | 239 | 2.3 | 3.8 | 5.3 | 0.5 | 0.9 | 1.2 | 0 | 0.2 | 0 | 0.5 | 0.9 | 1.2 | 8 | 13 | 19 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | -Bank A, B, C temporary take out by Adc |  | 19922 |  | 7248 | KLMFEP-33001
| SC_PM_NA_UPS_NA_1 (1).pdf | KLS | 14/10/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 34.8 | 41.6 | 210 |  |  | 267 | 268 | 0 | 0 | 0 | 255 | 254 | 256 | 254 | 254 | 255 | 239 | 240 | 240 | 2.5 | 5.9 | 6.3 | 0.6 | 0.8 | 1.4 | 10 | 0.2 | 0.2 | 0.5 | 0.9 | 1.5 | 8 | 13 | 22 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.7 | 12.6 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 100 | 60 | 80 | 120 | connection connector cable secure and system in good condition. |  | 7110 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA (9).pdf | KLS | 2025-01-14 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 214 | 50.05 | 50 | 267 | 268 | 0 | 0 | 0 | 255 | 253 | 256 | 254 | 256 | 255 | 239 | 238 | 239 | 2.3 | 4.7 | 5.8 | 0.5 | 0.9 | 1.3 | 0 | 0.2 | 0 | 0.5 | 1 | 1.3 | 8 | 16 | 20 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | The UPS only use one bank and one breaker. Everything is in good condition. This up's also use two module. |  | 22778 |  | 7110 | KLMFEP-33001
| SC_PM_NA_UPS_NA_10.pdf | KLS | 14/07/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 32.1 | 40.3 | 212 |  |  | 269 | 270 | 0 | 0 | 0 | 257 | 255 | 258 |  |  |  | 239 | 238 | 239 | 2.3 | 4.2 | 5.7 | 0.5 | 0.8 | 1.3 | 0 | 0.2 | 0.1 | 0.5 | 0.8 | 1.2 | 8 | 14 | 19 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All in good condition |  | 20450 |  | 7262 | KLMFEP-33001
| SC_PM_NA_UPS_NA (1).pdf | KLS | 14/07/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 40.1 |  | 49 | 14 | 50 | 20.7 | 24.8 | 0 | 0 | 0 | 248 | 248 | 247 | 249 | 248 | 248 | 230 | 230 | 231 | 5.3 | 5.3 | 10.3 | 1.2 | 1.2 | 2.3 | 0.3 | 0.1 | 0.4 | 1.2 | 1.2 | 2.3 | 19 | 10 | 25 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.7 | 12.05 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 100 | 60 | 50 | 120 |  |  | 7222 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA (5).pdf | KLS | 14/04/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 34.1 | 40.9 | 104 |  |  | 268 | 268 | 0 | 0 | 0 | 256 | 254 | 257 | 255 | 254 | 257 | 239 | 239 | 240 | 5 | 8.1 | 12.1 | 1.1 | 1.9 | 2.6 | 0.3 | 0.6 | 0.5 | 1.1 | 1.9 | 2.7 | 17 | 29 | 41 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipment in good Condition |  | 20449 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_1 (2).pdf | KLS | 14/04/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36.7 |  | 107 |  |  | 268 | 268 | 0 | 0 | 0 | 253 | 253 | 254 | 253 | 253 | 254 | 240 | 239 | 240 | 5 | 7.9 | 11.3 | 1.1 | 1.5 | 2.8 | 0.3 | 0.5 | 10.5 | 1.2 | 1.8 | 2.8 | 17 | 22 | 42 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.3 | 12.1 | 12.2 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 102 | 100 | 60 | 50 | 40 | 1 Module Foil/problem |  | 7223 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA.pdf | KLS | 14/04/2022 |  | TRUE | TRUE | TRUE | TRUE |  | 100 | 32.2 | 38.9 | 150 |  |  | 271 | 271 | 0 | 0 | 0 | 248 | 248 | 248 |  |  |  | 239 | 239 | 240 | 20 | 6.9 | 10.3 | 0.4 | 1.4 | 2.4 | 0 | 0.2 | 0.5 | 0.5 | 1.4 | 2 | 7 | 23 | 36 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 13.4 | 13.4 | 13.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  | 150 | 100 | 80 | 80 | 50 | all equitment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA (8).pdf | KLS | 14/01/2025 |  | TRUE | TRUE | TRUE | TRUE |  | 100 |  |  | 214 |  |  | 267 | 268 | 0 | 0 | 0 | 255 | 253 | 256 | 254 | 256 | 255 | 239 | 238 | 239 | 2.3 | 4.7 | 5.8 | 0.5 | 0.9 | 1.3 | 0 | 0.2 | 0 | 0.5 | 1 | 1.3 | 8 | 16 | 20 | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | The UPS only use one bank and one breaker. Everything is in good condition. This ups also use two module. |  | 22778 |  | 7110 | KLMFEP-33001
| SC_PM_NA_UPS_NA (4).pdf | KLS | 14/01/2024 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 34.2 | 40.9 | 101 |  |  | 268 | 268 | 0 | 0 | 0 | 256 | 256 | 258 | 256 | 256 | 257 |  |  |  | 4.9 | 7.6 | 11.8 | 1.1 | 1.9 | 2.8 | 0.3 | 0.6 | 0.5 | 1.2 | 1.8 | 2.8 | 17 | 27 | 40 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | All equipment is in good condition |  | 19898 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_2.pdf | KLS | 14/01/2023 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 28 | 38.2 | 270 | 50 | 50 | 268 | 263 | 0 | 0 | 0 | 234 | 233 | 235 | 236 | 334 | 239 | 240 | 240 | 240 | 1.6 | 4.7 | 3.7 | 0.4 | 1 | 0.8 | 0 | 0.2 | 0.1 | 0.3 | 1.1 | 0.8 | 5 | 15 | 14 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.8 | 12.6 | 12.7 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 200 | 100 | 100 | 50 | 100 | all equipment in good conditions |  | 11727 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_1.pdf | KLS | 14/01/2022 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 24 |  | 240 |  |  | 260 | 261 | 0 | 0 | 0 | 271 | 272 | 273 | 240 | 241 | 242 | 1.5 | 1.4 | 1.3 | 0.3 | 1.2 | 0.4 | 0.3 | 0.1 | 0.9 | 0.1 | 0.1 | 0 | 0.2 | 1 | 1 | 5 | 14 | 9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 12.6 | 12.4 | 12.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | 240 | 100 | 120 | 50 | 120 | OK |  | 7110 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA (3).pdf | KLS | 2023-04-07 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 65 |  | 105 | 50 | 50 | 268 | 268 | 0 | 0 | 0 | 254 | 254 | 255 | 254 | 254 | 255 | 240 | 239 | 239 | 4.8 | 7.6 | 11.5 | 1.1 | 1.8 | 2 | 0.3 | 0.5 | 0.4 | 1.1 | 1.9 | 2.7 | 17 | 28 | 45 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [5 empty] | good condition |  | 7223 |  | 7111 | KLMFEP-33001
| SC_PM_NA_UPS_NA_14.pdf | OCC | [83 empty] | KLMFEP-33001

## psd
workorder_id | filename | station | date_time | pm_order | checklist_items.safety_and_preparation.make_sure_safety_precautions_procedures_being_followed_as_required..status | checklist_items.safety_and_preparation.inform_occ_before_start_any_task..status | checklist_items.general_inspection.perform_visual_inspection_and_confirm_all_cable_properly_connected..status | checklist_items.general_inspection.confirm_both_of_module_is_on_and_inverter_mode..status | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.status | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.A_battery_capacity | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.B_module_temp.in | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.B_module_temp.out | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.C_battery_run_time | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.D_output_freq_hz | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.E_bypass_freq_hz | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.F_battery_voltage_v.positive | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.F_battery_voltage_v.negative | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.G_battery_charge_car_a.positive | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.G_battery_charge_car_a.negative | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.H_discharge_current_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.I_rectifier_voltage_v_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.I_rectifier_voltage_v_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.I_rectifier_voltage_v_c | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.J_bypass_voltage_v_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.J_bypass_voltage_v_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.J_bypass_voltage_v_c | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.K_output_voltage_v_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.K_output_voltage_v_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.K_output_voltage_v_c | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.L_output_current_a_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.L_output_current_a_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.L_output_current_a_c | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.M_active_power_kw_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.M_active_power_kw_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.M_active_power_kw_c | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.N_reactive_power_kva_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.N_reactive_power_kva_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.N_reactive_power_kva_c | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.O_apparent_power_kva_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.O_apparent_power_kva_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.O_apparent_power_kva_c | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.P_output_power_percent_a | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.P_output_power_percent_b | checklist_items.general_inspection.using_scroll_arrow_scroll_and_record_as_below.readings.P_output_power_percent_c | checklist_items.servicing_and_cleaning.set_the_ups_to_maintenance_bypass_mode_by_using_command_from_module..status | checklist_items.servicing_and_cleaning.switching_on_switch_maintenance_bypass_in_front_of_ups_rack..status | checklist_items.servicing_and_cleaning.confirm_the_display_panel_is_showing_bypass_mode..status | checklist_items.servicing_and_cleaning.switch_off_all_battery_breakers..status | checklist_items.servicing_and_cleaning.switch_off_both_of_module_using_2_finger_push_button_on_off..status | checklist_items.servicing_and_cleaning.open_screw_and_pull_both_of_module_to_cleaning..status | checklist_items.servicing_and_cleaning.open_screws_each_battery_bank_and_check_the_voltage..status | checklist_items.servicing_and_cleaning.wait_for_the_electrolytic_condensers_on_the_power_board_to_discharge_wait_at_least_15min_before_proceed_any_maintenance_work..status | checklist_items.servicing_and_cleaning.randomly_check_the_voltages_on_the_batteries._ensure_minimum_voltage_is_read_as_12v_and_maximum_should_not_be_more_than_13.8v..status | checklist_items.servicing_and_cleaning.check_end_to_end_batteries_voltages..status | checklist_items.servicing_and_cleaning.do_the_cleaning_on_all_the_batteries._confirm_and_ensure_no_cable_is_disconnected_from_any_terminals..status | checklist_items.servicing_and_cleaning.after_completed_the_cleaning_confirm_all_cablings_are_secured_and_in_the_correct_position..status | checklist_items.servicing_and_cleaning.switch_on_both_of_module_using_2_finger_push_button_on_off..status | checklist_items.servicing_and_cleaning.button_on_off..status | checklist_items.servicing_and_cleaning.normalized_all_battery_breakers..status | checklist_items.servicing_and_cleaning.switch_off_switch_maintenance_bypass_in_front_of_ups_rack..status | checklist_items.servicing_and_cleaning.set_the_ups_to_inverter_mode_by_using_command_from_module..status | checklist_items.servicing_and_cleaning.confirm_with_occ_no_alarm_is_activated_on_scada..status | checklist_items.servicing_and_cleaning.check_and_see_is_everything_back_to_normal..status | checklist_items.battery_backup_test.before_proceed_this_test_make_sure_battery_level_should_be_above_80%_of_load..status | checklist_items.battery_backup_test.confirm_ups_in_inverter_mode_and_no_alarm_activated..status | checklist_items.battery_backup_test.turn_off_main_switch_breaker_for_main_incoming_supply..status | checklist_items.battery_backup_test.confirm_after_a_few_seconds_alarm_sounding_"battery_working"_led_illuminate_and_ups_change_to_"battery_mode"..status | checklist_items.battery_backup_test.observe_the_ups_time_remaining_and_battery_percentage..status | checklist_items.battery_backup_test.switch_on_back_main_switch_breaker_after_ups_reaching_50%_of_battery_level..status | comments_recommendation | performed_by.name | performed_by.id | verified_by.name | verified_by.id | reference_document
4000672868 | PS_PM_QTR_UPSSystem_4000672868.pdf | MAH | 16/04/2025 |  | TRUE | TRUE | TRUE | TRUE | [36 empty] | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | All in good condition | IZZUDDIN | 22388 | MOHD IRZAN | 7094 | KLMFEP-33001
4000672871 | PS_PM_QTR_UPSSystem_4000672871.pdf | MKU | 22/04/2025 |  | TRUE | TRUE |  | TRUE | TRUE | 100 | 37.9 |  | 261 | 50.06 | 50 | 268 | 249 | 0 | 0 | 0 | 233 | 234 | 237 | 235 | 264 | 237 | 239 | 240 | 240 | 1.4 | 4.3 | 3.6 | 0.3 | 0.2 | 0.2 | 0.3 | 1 | 0.9 | 0.3 | 1 | 0.9 | 4 | 15 | 14 |  |  |  | TRUE |  | TRUE |  |  |  | TRUE |  |  |  | TRUE | TRUE |  |  | TRUE | TRUE | [6 empty] | All in good condition | M. ISKANDAR | 20157 | NORIEZUWADI | 19234 | KLMFEP-33001
4000690941 | PS_PM_QTR_UPSSystem_4000690941.pdf | DCC | 26/07/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 98.7 | 25.5 | 27 |  | 50 | 50 | 268 | 267.4 | [6 empty] | 241.6 |  |  | 240.4 |  |  | 32 |  |  | 8.4 |  |  | 9.1 |  |  | 9 |  |  | 30.3 |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | IN GOOD CONDITION | M. ISKANDAR | 20157 | NORIEZUWADI | 19234 | KLMFEP-33001
4000672874 | PS_PM_QTR_UPSSystem_4000672874.pdf | HAH | 17/04/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 36 |  | 352 | 50 | 50 | 2.67 | 2.67 |  |  |  | 240 | 239 | 242 | 241 | 239 | 245 | 240 | 239 | 246 | 1.4 | 3.4 | 2.5 | 0.3 | 0.8 | 0.5 | 0 | 0.1 | 0.1 | 0.3 | 0.8 | 0.6 | 5 | 11 | 9 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | All in good condition | IZZUDIN | 22388 | MOHD IRZAN | 7094 | KLMFEP-33001
4000673151 | PS_PM_QTR_UPSSystem_4000673151.pdf | OCC | 25/04/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 25.5 | 27 | 173 | 49.95 | 49.96 | 267.5 | 267.5 | 0 | 0.1 |  | 246.7 | 245.8 | 245.4 | 246.8 | 246 | 245.2 | 230 | 230 | 230 | 2.8 | 4.2 | 4.5 | 0.5 | 0.9 | 0.9 | 0.6 | 1 | 1.1 | 2.5 | 3.9 | 4 | 19.3 | 29 | 31.3 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | PM inspection already make by group Jurij and also tonight has test train so mainline remain ON. | SUFFI SHUKHAIRI | 20971 | JURIS | 19924 | KLMFEP-33001
4000673149 | PS_PM_QTR_UPSSystem_4000673149.pdf | TSA | 24/04/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 35.9 |  | 205 | 49.99 | 50 | 226 | 226 | 0 | 0 | 0 | 240 | 241 | 243 | 241 | 241 | 243 | 240 | 239 | 239 | 1.5 | 3.4 | 3.7 | 0.3 | 1.2 | 1.3 | 0.1 | 0.2 | 0.3 | 0 | 1.2 | 1.4 | 20 | 20 | 20 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | All in good condition | M.ISKANDAR | 20157 | NORIEZUWADI | 19234 | KLMFEP-33001
4000672877 | PS_PM_QTR_UPSSystem_4000672877.pdf | RAN | 20/04/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 32.1 |  | 238 | 50.03 | 50 | 266 | 266 | 0 | 0 | 0 | 246 | 244 | 245 | 244 | 243 | 246 | 239 | 240 | 239 | 2.2 | 3.8 | 4.9 | 0.5 | 0.8 | 1.2 | 0 | 0.2 | 0.1 | 0.5 | 1 | 1.1 | 7 | 12 | 17 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | All in good condition | IZZUDDIN | 22388 | MOHD IRZAN | 7094 | KLMFEP-33001
4000673152 | PS_PM_QTR_UPSSystem_4000673152.pdf | DCC | 26/04/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  | 50 | 50 | 50 | 26.8 | 26.8 | 0 | 0 | 0 | 242 | 242 | 245 | 242 |  |  | 240 |  |  | 38.8 | [5 empty] | 3.7 |  |  | 8.9 | [5 empty] | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | All in good condition | SUFFI SHUKHAIRI | 20971 | AHMAD JURIS | 19924
4000672878 | PS_PM_QTR_UPSSystem_4000672878.pdf | BAS | 21/04/2025 |  | TRUE | TRUE |  | TRUE | TRUE | 100 |  |  | 195 | 49.99 | 50 |  |  |  |  | 0 | 246 | 246 | 248 | 246 | 240 | 248 | 240 | 240 | 240 | 1.5 | 3.5 | 5.7 | 0.3 | 0.9 | 1.4 | 0 | 0.2 | 0.2 | 0.3 | 0.8 | 1.4 | 5 | 12 | 0.1 |  |  |  | TRUE |  | TRUE |  |  |  | TRUE |  |  |  |  | TRUE |  |  | TRUE | TRUE | [6 empty] | All in good condition |  | 20157 |  | 19234 | KLMFEP-33001
4000672876 | PS_PM_QTR_UPSSystem_4000672876.pdf | BNG | 19/04/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 33.6 |  | 600 | 50.04 | 50 | 266 | 266 | 0 | 0 | 0 | 243 | 243 | 246 | 244 | 243 | 246 | 239 | 239 | 240 | 2.3 | 6.2 | 4 | 0.5 | 1.5 | 0.3 | 0.2 | 0.2 | 0.1 | 0.6 | 1.5 | 0.3 | 9 | 25 | 13 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | All in good condition | IZZUDDIN | 22388 | MOHD IRZAN | 7094 | KLMFEP-33001
4000672879 | PS_PM_QTR_UPSSystem_4000672879.pdf | CIT | 23/04/2025 |  | TRUE | TRUE |  | TRUE | TRUE | 100 |  |  | 451 | 49.98 | 80 |  |  |  |  | 0 | 246 | 245 | 245 | 246 | 245 | 245 | 239 | 240 | 239 | 0.8 | 1.7 | 2.2 | 0.1 | 0.3 | 0.7 | 0 | 0.4 | 0.1 | 0.1 | 0.4 | 0.2 | 0 | 5 | 11 |  |  |  | TRUE |  | TRUE |  |  |  | TRUE |  |  |  |  | TRUE |  |  | TRUE | TRUE | [6 empty] | All in good condition | ISKANDAR | 20157 | NORIEZUWADI | 19234 | KLMFEP-33001
4000673949 | PS_PM_QTR_UPSSystem_4000673949.pdf | TUN | 15/04/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 |  |  |  | 50.01 | 50.03 |  |  |  |  | 0 | 50 | 1 | 33 | 240 | 241 | 243 | 241 | 241 | 240 | 0.2 | 0.3 | 1.9 | 0.1 | 0.4 | 0.3 | 0.5 | 2 | 1.5 | 0.3 | 1 | 1 | 8.3 | 16.3 | 15.4 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | All in good condition | IZUDDIN | 22388 | MOHD IRZAN | 7094
4000675828 | PS_PM_QTR_UPSSystem_4000675828.pdf | KLS | 14/04/2025 |  | TRUE | TRUE | TRUE | TRUE | TRUE | 100 | 34.6 | 41.3 | 212 | 49.98 | 50 |  |  |  |  | 0 | 257 | 256 | 258 | 257 | 256 | 258 | 240 | 239 | 240 | 2.3 | 4.6 | 5.4 | 0.5 | 1 | 1.3 | 0.1 | 0.4 | 0.2 | 0.5 | 1 | 1.3 | 9 | 14 | 20 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | All in goud Condition | SHAHIN AMMAR | 20610 | DINESH | 7114 | KLMFEP-33001
4000672875 | PS_PM_QTR_UPSSystem_4000672875.pdf | IBI | 18/04/2025 |  | TRUE | TRUE |  | TRUE | [39 empty] | TRUE |  | TRUE |  |  |  | TRUE |  | TRUE |  |  | TRUE |  | TRUE | TRUE | TRUE | [5 empty] | TRUE | All in good conditon | IZZUDDIN | 22388 | MOHD IRZAN | 7094 | KLMFEP-33001