## ups_system
station | date_time | pm_order | checklist_items.safety_and_preparation.a.description | checklist_items.safety_and_preparation.a.status | checklist_items.safety_and_preparation.b.description | checklist_items.safety_and_preparation.b.status | checklist_items.safety_and_preparation.remarks | checklist_items.general_inspection.a.description | checklist_items.general_inspection.a.status | checklist_items.general_inspection.b.description | checklist_items.general_inspection.b.status | checklist_items.general_inspection.c.description | checklist_items.general_inspection.c.status | checklist_items.general_inspection.c.readings.A_battery_capacity | checklist_items.general_inspection.c.readings.B_module_temp | checklist_items.general_inspection.c.readings.C_battery_run_time | checklist_items.general_inspection.c.readings.D_output_freq_hz | checklist_items.general_inspection.c.readings.E_bypass_freq_hz | checklist_items.general_inspection.c.readings.F_battery_voltage_v.positive | checklist_items.general_inspection.c.readings.F_battery_voltage_v.negative | checklist_items.general_inspection.c.readings.G_battery_charge_car_a.positive | checklist_items.general_inspection.c.readings.G_battery_charge_car_a.negative | checklist_items.general_inspection.c.readings.H_discharge_current_a | checklist_items.general_inspection.c.readings.I_rectifier_voltage_v | checklist_items.general_inspection.c.readings.J_bypass_voltage_v | checklist_items.general_inspection.c.readings.K_output_voltage_v | checklist_items.general_inspection.c.readings.L_output_current_a | checklist_items.general_inspection.c.readings.M_active_power_kw | checklist_items.general_inspection.c.readings.N_reactive_power_kva | checklist_items.general_inspection.c.readings.O_apparent_power_kva | checklist_items.general_inspection.c.readings.P_output_power_percent | checklist_items.general_inspection.remarks | checklist_items.servicing_and_cleaning.a.description | checklist_items.servicing_and_cleaning.a.status | checklist_items.servicing_and_cleaning.b.description | checklist_items.servicing_and_cleaning.b.status | checklist_items.servicing_and_cleaning.c.description | checklist_items.servicing_and_cleaning.c.status | checklist_items.servicing_and_cleaning.d.description | checklist_items.servicing_and_cleaning.d.status | checklist_items.servicing_and_cleaning.e.description | checklist_items.servicing_and_cleaning.e.status | checklist_items.servicing_and_cleaning.f.description | checklist_items.servicing_and_cleaning.f.status | checklist_items.servicing_and_cleaning.g.description | checklist_items.servicing_and_cleaning.g.status | checklist_items.servicing_and_cleaning.h.description | checklist_items.servicing_and_cleaning.h.status | checklist_items.servicing_and_cleaning.h.battery_readings.battery1 | checklist_items.servicing_and_cleaning.h.battery_readings.battery2 | checklist_items.servicing_and_cleaning.h.battery_readings.battery3 | checklist_items.servicing_and_cleaning.i.description | checklist_items.servicing_and_cleaning.i.status | checklist_items.servicing_and_cleaning.j.description | checklist_items.servicing_and_cleaning.j.status | checklist_items.servicing_and_cleaning.k.description | checklist_items.servicing_and_cleaning.k.status | checklist_items.servicing_and_cleaning.l.description | checklist_items.servicing_and_cleaning.l.status | checklist_items.servicing_and_cleaning.m.description | checklist_items.servicing_and_cleaning.m.status | checklist_items.servicing_and_cleaning.n.description | checklist_items.servicing_and_cleaning.n.status | checklist_items.servicing_and_cleaning.o.description | checklist_items.servicing_and_cleaning.o.status | checklist_items.servicing_and_cleaning.p.description | checklist_items.servicing_and_cleaning.p.status | checklist_items.servicing_and_cleaning.q.description | checklist_items.servicing_and_cleaning.q.status | checklist_items.servicing_and_cleaning.r.description | checklist_items.servicing_and_cleaning.r.status | checklist_items.servicing_and_cleaning.s.description | checklist_items.servicing_and_cleaning.s.status | checklist_items.servicing_and_cleaning.t.description | checklist_items.servicing_and_cleaning.t.status | checklist_items.servicing_and_cleaning.u.description | checklist_items.servicing_and_cleaning.u.status | checklist_items.battery_backup_test.a.description | checklist_items.battery_backup_test.a.status | checklist_items.battery_backup_test.b.description | checklist_items.battery_backup_test.b.status | checklist_items.battery_backup_test.c.description | checklist_items.battery_backup_test.c.status | checklist_items.battery_backup_test.d.description | checklist_items.battery_backup_test.d.status | checklist_items.battery_backup_test.e.description | checklist_items.battery_backup_test.e.status | checklist_items.battery_backup_test.f.description | checklist_items.battery_backup_test.f.status | checklist_items.battery_backup_test.battery_backup_test.before.time_minutes | checklist_items.battery_backup_test.battery_backup_test.before.battery_percentage | checklist_items.battery_backup_test.battery_backup_test.after.time_minutes | checklist_items.battery_backup_test.battery_backup_test.after.battery_percentage | checklist_items.battery_backup_test.battery_backup_test.battery_backup_time_minutes | comment_recommendation | performed_by | verified_by | reference_document_no | workorder_id | filename
BNG | 19/04/2024 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 31.4, 36.5 | 10h 27m | 50 | 50 | 266 | 267 | 0.0 | 0.0 | 0.0 | 243, 242, 245 | 244, 242, 246 | 240, 240, 239 | 2.7, 6.5, 3.9 | 0.6, 0.5, 0.7 | 0.0, -0.1, 0.0 | 0.6, 0.4, 1.7 | 9, 22, 12 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on SCADA. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, “Battery Working” LED illuminate and UPS change to “BATTERY MODE”. | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | [5 empty] | ADC change 2 module UPS. Bank 3 dosnt have batteries. Module and all batteries in good condition. | 19921 | 7111 | KLMFEP-33001 | 4000608017 | SC_PM_QTR_UPS_4000608017.pdf
IBI | 18/01/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 31.5, 38.1 | 2HR | 50.03Hz | 50.00 Hz | 268 | 268 | 0.0 | 0.0 | 0.0 | 245, 246, 249 | 245, 246, 248 | 239, 239, 240 | 3.2, 6.5, 10.7 | 0.7, 1.4, 2.5 | 0.0, -0.5, -0.5 | 0.7, 1.6, 2.5 | 11, 23, 38 | - Module PO1 notified alarm Inverter Phase Fault. | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on SCADA. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | -Module P2 notified alarm Phase Fault -there are serval Faulty battery burn -beside that hardware in good condition - Bank 1 and 2 kembung | 20079 | 7111 | KLMFEP-33001 | 4000597779 | SC_PM_QTR_UPS_4000597779.pdf
| 19/01/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 32.8, 35.7 | 53 | 50.04 | 50 | 266 | 266 | 0.0 | 0.0 | 0.0 | 248, 246, 250 | 247, 246, 250 | 239, 239, 240 | 3.0, 6.6, 4.0 | 0.7, 1.6, 0.9 | 0.0, -0.2, 0.0 | 0.7, 1.6, 1.0 | 11, 24, 15 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on SCADA. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | Module need to calibrate. All battery in good condition. | 20452 | 7111 | KLMFEP-33001 | 4000597708 | SC_PM_QTR_UPS_4000597708.pdf
Tun | 15/10/2023 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 |  |  | 50 | 50 | 261 | 261 | 0.0 | 0 |  |  | 243, 242, 244 | 241, 241, 241 | 1.0, 8.1, 6.5 | 0.2, 1.6, 1.1 | 0.1, 2.0, 1.6 | 0.0, 0.8, 1.0 | 0.8, 0.84, 0.75 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 13.2 | 13.4 | 13.5 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | TRUE | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, Battery Working LED illuminate and UPS change to BATTERY MODE. | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 3h 6m | 100 | 1h 8m | 50 | 60 | good condition | 7248 | 7111 | KLMFEP-33001 | 4000576195 | SC_PM_QTR_UPS_4000576195.pdf
IBI | 18/10/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100% | 30,35.4 | 2 hour | 50.02 | 50 | +233 | -273 | + 0 | 0 | 0.0 | 252, 252, 256 | 252, 252, 254 | 239, 239, 239 | 2.9, 6.7, 11.3 | 0.7, 1.3,2.6 | 0.0,-05,-0.5 | 0.6,1.72.7 | 22,32,40 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 13.6 | 13.3 | 13.4 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. |  | Maximum should not be more than 13.8V. |  | Check end-to-end batteries voltages. |  | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. |  | After completed the cleaning, confirm all cablings. |  | Are secured and in the correct position. |  | Switch ON both of module using 2 finger push. |  | Button ON/OFF. |  | Normalized all battery breakers. |  | Switch OFF switch Maintenance bypass in front of UPS rack. |  | Set the ups to Inverter Mode by using command from module. |  | Confirm with OCC no alarm is activated on Scada. |  | Check and see is everything back to normal. |  | Before proceed this test, make sure battery level should be above 80% of load. |  | Confirm UPS in Inverter Mode and no alarm activated. |  | Turn OFF Main Switch Breaker for Main Incoming Supply. |  | Confirm after a few seconds, alarm sounding, Battery Working LED illuminate and UPS change to BATTERY MODE. |  | Observe the UPS time remaining and battery percentage. |  | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | [6 empty] | Slave module faulty only use 1 bank batteries | 19898 | 7111 | KLMFEP-33001 | 4000576144 | SC_PM_QTR_UPS_4000576144.pdf
BAS | 21/10/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100% |  | 4h 10m | 50.03 | 50 | 266 | 266 | 0.0 | 0.0 | 0.0 | 247, 248, 250 | 247, 248, 250 | 239, 240, 240 | 1.4, 3.6, 5.5 | 0.3, 0.8, 1.3 | 0.0, -0.2, -0.2 | 0.3, 0.7, 1.3 | 3, 12, 20 |  | Set the UPS to Maintenance Bypass Mode by using command from module. |  | Switching ON switch maintenance bypass in front of UPS rack. |  | Confirm the Display panel is showing BYPASS MODE. |  | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. |  | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. |  |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. |  | Maximum should not be more than 13.8V. |  | Check end-to-end batteries voltages. |  | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. |  | After completed the cleaning, confirm all cablings. |  | Are secured and in the correct position. |  | Switch ON both of module using 2 finger push. |  | Button ON/OFF. |  | Normalized all battery breakers. |  | Switch OFF switch Maintenance bypass in front of UPS rack. |  | Set the ups to Inverter Mode by using command from module. |  | Confirm with OCC no alarm is activated on SCADA. |  | Check and see is everything back to normal. |  | Before proceed this test, make sure battery level should be above 80% of load. |  | Confirm UPS in Inverter Mode and no alarm activated. |  | Turn OFF Main Switch Breaker for Main Incoming Supply. |  | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". |  | Observe the UPS time remaining and battery percentage. |  | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | [6 empty] | All equipment in good condition | 20160 | 7111 | KLMFEP-33001 | 4000576104 | SC_PM_QTR_UPS_4000576104.pdf
BNG | 19/04/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 46.0, 50.9 | 54m | 50.02 | 50.09 | 266 | 266 | 0.0 | 0 | 0.0 | 246, 243, 246 | 245, 243, 247 | 240, 239, 240 | 2.7, 5.5, 3.5 | 0.6, 1.2, 0.7 | -0.1, -0.2, 0.1 | 0.6, 1.2, 0.8 | 10, 101, 12 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 13.4 | 12.8 | 13.9 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 55 | 100 | 25 | 50 | 55 | all equipment in good conditions | 11727 | 7111 | KLMFEP-33001 | 4000530667 | SC_PM_QTR_UPS_4000530667.pdf
TUN | 15/04/2023 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 |  | 54 | 49.9 | 49.5 | 249 | 269 |  |  |  |  | 240, 239, 241 | 241, 241, 247 | 1.9, 8.2, 6.4 | 0.1, 0.5, 0.5 |  | 0.5, 0.5, 0.4 |  |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 12.6 | 12.3 | 12.4 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of loud. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 5h | 100 | 3h | 60 | 10 |  | 7223 | 7111 | KLMFEP-33001 | 4000520523 | SC_PM_QTR_UPS_4000520523.pdf
BAS | 21/01/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100% | 31.5, 38.4 | 3h 45m | 50 | 50 | 266 | 266 | 0.0 | 0.0 | 0.0 | 249, 249, 249 | 249, 249, 250 | 240, 240, 240 | 1.5, 3.8, 6.0 | 0.3, 0.8, 1.4 | 0.0, 0.0, 0.3 | 0.3, 0.8, 1.4 | 5, 12, 22 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 13.6 | 13.6 | 13.4 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 200 | 100 | 100 | 50 | 100 |  | 7222 | 7111 | KLMFEP-33001 | 4000509125 | SC_PM_QTR_UPS_4000509125.pdf
RAN | 20/04/2024 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100% | 36.8, 41.5 | 3h 50m | 50.04 | 50 | 266 | 266 | 0.0 | 0.0 | 0.0 | 242, 242, 244 | 243, 241, 244 | 240, 240, 240 | 1.8, 3.8, 5.3 | 0.4, 0.8, 1.3 | 0.0, -0.2, -0.1 | 0.4, 0.9, 1.2 | 6, 14, 19 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of UPS rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on SCADA. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | [5 empty] | Module and battenes in good condition. Bank 2 and 3 don't have batteries Only used Bank 1. | 19921 | 7111 | KLMFEP-33001 | 4000608067 | SC_PM_QTR_UPS_4000608067.pdf
BAS | 21/07/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100% | 28.3,32.9 | 4h 28m | 50.02 (50/60Hz) | 50 (50/60Hz) | 266 | -266 | 0 | 0 | 0.0 | 248,247,252 | 248,247,252,(400) | 240,240,241,(3000VA) | 1.3,2.9,5.1,(43 A) | 0.3,0.6,1.1 | 0.0,-0.1,-0.1 | 0.3,0.7,1.1 | 4,11,17 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | All equipment are in good condition. | 20005 | 7223 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_1 (6).pdf
TUN | 15/01/2025 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100% | 30.2, 31.3 | 3h 50m | 50.5 (50/60Hz) | 50.00 (50/60Hz) | +267 | -268 | +0.0 | -0.0 | 0.0 | 244, 243, 246 | 244, 244, 247 (400) | 239, 239, 239 (3000VA) | 2.7, 6.2, 9.6 (43 A) | 08, 0.7, 2.3 | 0.1, 0.7, 2.3 | 0.8, -2.6, -2.2 | 12, 23, 34 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of UPS rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the UPS to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on SCADA. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, Battery Working LED illuminate and UPS change to BATTERY MODE. | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | [5 empty] | all equiptment in good conditions | 11727 | 11727 | KLMFEP-33001 | 4000668027 | SC_PM_QTR_UPS_4000668027.pdf
IBI | 18/04/2022 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | 1 unit module faults (share module) | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100% | 36.4, 44.4 | 2h 17m | 50 | 50 | 206 | 286 | 0 | 0 | 0 | 250 250 254 | 250,250 254 | 239,259,239 | 3.2, 6., 7.4 | 0.7, 1.5, 2.0 | 0.0, -0.4, -0.2 | 0.7, 1.6, 1.9 | 11, 23, 29 | 1 unit module faults (share module) | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 12.6 | 12.4 | 12.7 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 150 | 100 | 80 | 50 | 150 | OK | 7110 | 7111 | KLMFEP-33001 | 4000467087 | SC_PM_QTR_UPS_4000467087.pdf
BAS | 21/04/2022 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 | 29.3, 36.6 | 4H 32m | 80 | 50 | 267 | -268 | 1.0 | -0.0 | 0.0 | 248, 248, 250 | 248, 248, 254 | 240, 240, 240 | 1.5, 3.5, 4.5 | 0.3, 0.7, 1.0 | -0.0, -0-1, 0.1 | 0.3, 0.0, 1.0 | s, 11, 16 | 2 bank battery temporary faulty | Set the UPS to Maintenance Bypass Iviode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 12.0 Volt | 12.9 Volt | 13.2 Volt | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 180 | 100 | 80 | 50 | 80 | ok | 7110 | 7111 | KLMFEP-33001 | 4000467064 | SC_PM_QTR_UPS_4000467064.pdf
KLS | 14/07/2024 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100% | 32.1, 40.3 | 3h 32m | 50 (50/60Hz) | 50 (50/60Hz) | 269 | 270 | 0.0 | 0.0 | 0.0 | 257, 255, 258 | 256,255,258 (400) | 239, 238, 239 (3000VA) | 2.3, 4.2, 5.7 (43 A) | 0.5, 0.8, 1.3 | 0.0,-0.2, -0.1 | 0.5, 0.8, 1.2 | 8, 14, 19 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [5 empty] | All in good condition | 20450 | 7262 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_10.pdf
HAH | 17/04/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 |  | 04h 14m | 50.5 | 50 | 267 | 267 | 0.1 | 0.1 | 0.0 | 239, 237, 240 | 238, 237, 240 | 239, 239, 240 | 1.6, 3.5, 3.7 | 0.4, 0.8, 0.7 | 0.0, 0.0, 0.0 | 0.3, 0.9, 0.7 | 5, 12, 11 | Bank 1 & Bank 2 dismantle further maintenance | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on SCADA. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | Bank 1 & Bank 2 dismantle further maintenance | 20449 | 7111 | KLMFEP-33001 | 4000608037 | SC_PM_QTR_UPS_4000608037.pdf
TUN | 15/01/2022 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 34 | 3h | 50 | 50 | 241 | 242 | 0.2 | 0.1 | 1.9 | 243,241,245 | 243,244,244 | 241,240,244 | 1.9,6.5.4 | 0.2,0.1,1.1 | 0.3,1.6,1.7 | 0.1,1.1.1.1 | 3.5,3.2,3.0 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 12.2 | 12.5 | 12.4 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 180 | 100 | 90 | 50 | 90 | ok | 7110 | 7111 | KLMFEP-33001 | 4000446286 | SC_PM_QTR_UPS_4000446286.pdf
OCC | 25/01/2022 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 48.1, 37.8 | 4h 30m | 50 | 49.9 | 207 | 240 | 0 | 0.0 | 0.0 | 248, 248, 248 | 249, 249, 239 | 238, 238, 239 | 5.3, 5.3, 10.2 | 1.2 1.2 2.3 | 0.3, -0.1, +0.4 | 1.2, 1.2, 2.5 | 14, 18, 36 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 12.6 | 12.6 | 12.6 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 180 | 100 | 90 | 50 | 80 | all equitment in good conditions | 11727 | 7111 | KLMFEP-33001 | 4000446335 | SC_PM_QTR_UPS_4000446335.pdf
MAH | 16/01/2022 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 34.1, 41.5 | 3h 16m | 80 | 80 | +271 | -271 | 0.0 | 0.0 | 0 | 255, 256, 254 | 255, 256, 254 | 229, 239, 239 | 3.2, 6.1, 7.6 | 0.7, 1.6, 1.8 | +0.0, -0.3, -0.5 | 0.7, 1.5, 1.8 | 11,23,27 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 12.8 | 12.6 | 12.7 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 240 | 100 | 120 | 50 | 120 | ok | 7222 | 7111 | KLMFEP-33001 | 4000446338 | SC_PM_QTR_UPS_4000446338.pdf
BI | 18/01/2022 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100% | 36.4,44.4 | 2h, 17m | 56 (50/60Hz) | SO (50/60Hz) | 286 | 286 | 0 | 0 | 0 | 280, 250, 254 | 280, 250, 254 | 239, 239, 239 | 3.2, 6.9, 7.7 | 0.7, 1.5, 2.0 | +0.0, -0.4, -0.2 | 0.7, 1.6, 1.9 | 11, 23, 29 | 1 unit module faulty. | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 12.6 | 12.8 | 12.7 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 160 | 100 | 80 | 50 | 80 | ok | 7222 | 7111 | KLMFEP-33001 | 4000446346 | SC_PM_QTR_UPS_4000446346.pdf
BFD | 26/01/2022 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 40.1, 38.8 | 5h 49m | 49 | 50 | 267 | 268 | 0.0 | 0.0 | 00 | 248, 248, 247 | 249, 248, 248, | 230, 238, 239 | 5.3, 5.5, 10.7 | 1.2, 1.2, 2.3 | 0.3, 0.1, 0.4 | 1.2, 1.2, 2.2 | 19, 10, 35 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 12.6 | 12.6 | 12.6 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true |  | 100 | 15 | 50 | 15 | equitment in good conditions but not view or display estimate time back up, -battery drain out very fast | 11727 | 7111 | KLMFEP-33001 | 4000446356 | SC_PM_QTR_UPS_4000446356.pdf
CIT | 23/01/2022 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 37.1, 44.8 | 5 hours 7 minutes | 50 | 50 | 268 | 269 | 0.0 | 0.1 | 0.0 | 240, 248, 249 | 248, 249, 240 | 240, 239, 239 | 1.0, 2.0, 3.0 | 0.2, 0.4, 0.7 | -0.1, 0.0, -0.1 | 0.2, 0.4, 0.7 | 3, 2, 11 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 12.6 | 12.4 | 13.2 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 120 | 100 | 60 | 50 | 120 | ok | 7223 | 7111 | KLMFEP-33001 | 4000446359 | SC_PM_QTR_UPS_4000446359.pdf
BNG | 19/01/2022 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100% | 45.8, 50.7 | 3h 40m | 50 (50/60Hz) | 50 (50/60Hz) | 270 | 270 | 0 | 0 | 0 | 249, 296, 249 | 248, 247, 280 | 239, 239, 240 | 2.7, 4.8, 3.9 | 0.6, 0.6, 1.0 | +0.0, -0.1, +0-0 | 0.6, 1.1, 1.0 | 10, 16, 14 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 12.6 | 12.7 | 12.8 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 80 | 100 | 40 | 50 | 40 | 2 battery book faulty | 7222 | 7111 | KLMFEP-33001 | 4000446363 | SC_PM_QTR_UPS_4000446363.pdf
BNG | 19/04/2022 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 | 46.2 | 3H 40m | 50 | 50 | +270 | 270 | + 0.0 | - 0.0 | 0 | 249, 246,249 | 248,247,230 | 239,239,240 | 2.7, 4.8, 3.9 | 0.6,0.6,1.0 | 0.0, -0.1, 0.0 | 0.6, 1.1, 1.0 | 10,16,14 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 12.6 | 12.7 | 12.6 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 100 | 100 | 50 | 50 | 90 | - 2 battery bank faulty | 7110 | 7111 | KLMFEP-33001 | 4000467069 | SC_PM_QTR_UPS_4000467069.pdf
CIT | 23/04/2022 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 % | 37.1, 448 | 5h 7m | 50 | 50 | 268 | 268 | 0.0 | -0.1 | 0.0 | 242, 242 249 | 248,249,240 | 241,239, 239 | 1.0, 2.0, 3.0 | 0.2,0.4,0.7 | -0.1, 0.1, -0.1 | 0.2,0.4,0.7 | 3,2,11 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 12.6Volt | 12.4 Volt | 13.2 Volt | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 160 | 100 | 80 | 50 | 80 | ok | 7222 | 7111 | KLMFEP-33001 | 4000467073 | SC_PM_QTR_UPS_4000467073.pdf
BFD | 26/04/2002 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100% | 40.1,38.8 | 5h,49m | 19 | 50 | 267,268 |  | 0.0 | 0.0 | 0.0 | 298,248,247 | 230,227,277 | 5.3, 5.5, 1.3 | 1.2, 1.2,2.3 | 0.3,0.1,0.4 | 0.3,0.1,0.4 | 1.2,1.2,2.2 | 19,10,37 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 12.6 | 12.6 | 12.6 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked |  | 100% | 15 | 50 | 15 | not displaayed time astimate | 14952 | 7111 | KLMFEP-33001 | 4000467077 | SC_PM_QTR_UPS_4000467077.pdf
MAH | 16/04/2022 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 | 32.2, 38.9 | 2h 13m | 50.01 | 50 | 271 | 271 | 0.0 | 0.0 | 0.0 | 248, 248, 248 | 248, 249, 249 | 239, 239, 240 | 2.0,, 6.9, 10.3 | 0.4, 1.4, 2.4 | 0.0, -0.2, -0.8 | 0.5, 1.4, 2.6 | 7, 23, 37 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 13.6 | 13.6 | 13.6 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 180 | 100 | 60 | 50 | 60 | all equipment in good conditions | 11727 | 7111 | KLMFEP-33001 | 4000467093 | SC_PM_QTR_UPS_4000467093.pdf
BAS | 21/01/2022 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 29.6, 36.6 | 4h 32m | 80 | 50 | 269 | 269 | 0.0 | 0 | 0.0 | 248, 248, 250 | 248, 248, 250 | 240, 240, 240 | 1.5, 3.5, 4.5 | 0.3, 0.7, 1.0 | -0.0, -0.1, -0.1 | 0.3, 0.6, 1.0 | 5, 11, 16 | 2 banh temperory faulty. | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 12.8 | 12.9 | 13.2 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 180 | 100 | 80 | 50 | 60 | ♡ | 7223 | 7111 | KLMFEP-33001 | 4000446126 | SC_PM_QTR_UPS_4000446126.pdf
RAN | 20/04/2022 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 | 49.5, 32.5 | 150 | 50 | 50 | 298, | 282 | 0.0 | -0.0 | 0.0 | 246, 247, 249 | 282,281,283 | 244,242,241 | -0.1, 0.1, 0.2 | 1.0, 1.1, 1.2 | 0.1, 0.2, 0.5 | 0.4, 0.7, 0.6 | 8, 16, 23 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 12.8 | 15.2 | 12.6 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 120 | 100 | 80 | 50 | 80 | ok | 7110 | 7111 | KLMFEP-33001 | 4000467101 | SC_PM_QTR_UPS_4000467101.pdf
MAH TUN | 16/04/2022 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 | 247, 226, 236 | 20353 H | 49.9 | 496 | 267 | -267 | 768.3 | -268.1 | 1.3 |  | 244,243,243 | 241,241,2141 | 0.2, 2.1, 1.5 | 0.4,1.9,2.4 | 0.0,-0.2-0.5 | 0.5,1.4 2.6 | 7,23,36 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 13.4 | 13.4 | 13.4 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 110 | 100 | 60 | 50 | 105 | all equipment in good conditions | 11727 | 7111 | KLMFEP-33001 | 4000467110 | SC_PM_QTR_UPS_4000467110.pdf
TSA | 24/01/2022 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 42 | 3h 5m | 30 | 50 | 272 | 268 | 0.0 | 0 | 0.0 | 238, 237, 240 | 238, 239, 240 | 240, 241, 244 | 1.6, 1.3, 4.4 | 0.3, 1.2, 1.0 | 0.1, 0.1, 0.2 | 0.4, 1.3, 1.0 | 5, 17, 15 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 13.6 | 13.6 | 13.6 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 200 | 100 | 110 | 80 | 110 | all equitment in good conditions. | Leam | 7111 | KLMFEP-33001 | 4000446312 | SC_PM_QTR_UPS_4000446312.pdf
BAS | 21/07/2022 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100% | 313, 38.3 | 3h 48m | 50.4 | 50 | +266 | -206 | 0.0 | -0.0 | 0 | 249, 249, 249 | 249, 249, 252 | 240, 240, 240 | 1.5, 3.8, 6.0 | 03, 09, 1.4 | 0.0, -0.0, -0.3 | 0.3, 0.8, 1.4 | 5.13.22 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 13.6 | 13.6 | 13 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, Battery Working LED illuminate and UPS change to BATTERY MODE. | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 190 | 100 | 100 | 50 | 100 | all equipment in good conditions | 11727 | 7111 | KLMFEP-33001 | 4000480661 | SC_PM_QTR_UPS_4000480661.pdf
BVG | 19/07/22 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 32.4,36.4 | 00 48m | 50 | 50 | +260 | -264 | 0.0 | 0 | 0.0 | 250,249,253 | 249, 244, 253 | 239,239,240 | 2.7,3.1,3.8 | 0.6,1.4,0.9 | +0.0,-0.2,+0.0 | 0.6, 1.4, 1.8 | 9,22,14 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 13.1 | 13.6 | 13.4 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 150 | 100 | 70 | 50 | 70 | all equitment in good condition | 11727 ABDUL AZIM | 7111 AZHAR YUNUS | KLMFEP-33001 | 4000480668 | SC_PM_QTR_UPS_4000480668.pdf
CIT | 23/7/22 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100% | 30.0,37.9 | 6h 23m | 50 (50/60Hz) | 50 (50/60Hz) | 266 | 268 | +0.0 | -0.0 | 0 | 239,240,241 | 240,239,241 | 240,239,239 | 240,239,239 | 1.1.1.9.3.9 | 0.2,0.5,0.9 | -0.1,+0.0,-0.1 | 0.2,0.5,0.9 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 13.7 Volt | 13.5 Volt | 13.4 volt | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode ana no alarrn activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 6H20M | 100 | 3h | 50 | 150 | Ok | 7110 SYAHRUL AZWAN | 7111 AZHAR YUNUS | KLMFEP-33001 | 4000480674 | SC_PM_QTR_UPS_4000480674.pdf
BFD | 26/07/2022 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 | 28 |  | 50 |  | 272 | 272 |  |  |  |  | 242 - (L-N) | 239 - (L-N) | 39.7 |  |  |  |  | Load: 50% Output power kva:9.5 output p kw:8.5 Autonomy time: ??? system temp: 28°c Main voltage: 417, 419, 420 current:-0.0,-0-0 peak current :108.3A | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 13.2 Volt | 13.4 Volt | 13.4 Volt | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked |  | 100% | 20 | 50% | 20 | not display time estimate | 7110 SYAHRUL AZWAN | 7111 AZHAR YUNUS | KLMFEP-33001 | 4000480679 | SC_PM_QTR_UPS_4000480679.pdf
RAN | 20/01/2022 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 48.5, 32.5 | 150m | 50 | 50 | 282 | 253 | 0.0 | 0.0 | 0.0 | 246, 247, 249 | 282, 281, 283 | 244, 242, 241 | -0.1, 0.1, 0.2 | 1.0, 1.1, 1.2 | 0.1, 0.2, 0.5 | 0.4, 0.7, 0.6 | 8, 1.6, 2.3 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 12.8 | 13.2 | 12.6 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 100 | 100 | 50 | 50 | 80 | ok | 7223 | 7111 | KLMFEP-33001 | 4000446322 | SC_PM_QTR_UPS_4000446322.pdf
HAH | 17/07/2022 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 36 | 6h 20m | 50 | 50 | 271 | 271 | 0.0 | -0.0 | 0.0 | 237,236, 239 | 237,236,239 | 238,239,239 | 1.4,2.3,2.7 | 0.3,0.5,0.6 | +0.0.+0.0,-0.1 | 0.3,0.5,0.6 | 8,8,9 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 12.5 | 12.6 | 12.8 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 2h 50m | 100 | 90m | 50 | 90 |  | 7223 ROHAIZAN | 7111 AZHAR YUNUS | KLMFEP-33001 | 4000480684 | SC_PM_QTR_UPS_4000480684.pdf
IBI | 18/07/2022 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 % | 36 | 2115m | 50 | 50 | 286 | 286 | 0.0 | 0.0 | 0 | 250,25,254 | 250,250,252 | 239,239,240 | 3.2,6.9,7.7 | 0.7,1.5,2.0 | +0.0,-0.4,-0.2 | -0.7,1.6,1.9 | 11,23,29 | I No dule with faulty | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 12.6 Volt | 12.8 Volt | 12.7 Volt | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 3h 10m | 100 | 80 | 50 | 80 | ok | 7223 ROHIZAN | 7111 AZHAR YUNUS | KLMFEP-33001 | 4000480689 | SC_PM_QTR_UPS_4000480689.pdf
RAN | 20/07/22 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100% | 34.5 40.6 | 3h 37m | 50 | 50 | 266 | -266 | 0.0 | 0.1 | 0 | 242,241,244 | 241,240,243 | 240,131,7 | 2.2,3.4,5.5 | 0.5,0.8,1.2 | 0.0,-0.1,-0.1 | 0.5,0.9,1.1 | 8,12,18 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 13.6 Volt | 13.4 Volt | 12.6 Volt | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 1.80 | 100 | 90 | 50 | 90 | all equitment in good conditions | 11727 ABDUL AZIN | 7111 AZHAR YUNUS | KLMFEP-33001 | 4000480709 | SC_PM_QTR_UPS_4000480709.pdf
TSA | 24/07/2022 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100% | 33.9,40.5 | 4h50m | 50 | 50 | 266 | 266 | 0.0 | 0.0 | 0.0 | 240,241,243 | 240,241,242 | 240, 239, 240 | 1.0,4.1,4.9 | 0.2,1.0,1.1 | +0.0,+0.0,-0.2 | 0.2,1.0,1.2 | 4,16,17 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 13.4 volt | 13.3 Volt | 13.4 Volt | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no ularn activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 9h00m | 100% |  |  |  | ups faulty\alarm battery discharge appear\must battery broken emporary maintanance bypass | 7110 SYAHRUL AZWAN | 7111 AZHAR YUNUS | KLMFEP-33001 | 4000480715 | SC_PM_QTR_UPS_4000480715.pdf
TSA | 24/4/2022 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 | 42 | 3h5 | 50 | 50 | 212 | 268 | 0.0 | 0.0 | 00 | 238,237,240 | 238,239,240 | 240,241,244 | 1.6,1.5,4.4 | 0.3,1.2,1.0 | 0.1,0.1,0.2 | 0.4,1.3,1.0 | 5,17,15 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 13.6 Volt | 13.6 Volt | 13.6 Volt | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 180 | 100 | 90 | 50 | 90 | ok. | 7222 MOHD RAZIF | 7111 AZHAR YUNUS | KLMFEP-33001 | 4000480717 | SC_PM_QTR_UPS_4000480717.pdf
TUN | 15/07/2022 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 | 33 | 3H | 50 | 50 | 241 | 242 | 0.2 | 0.1 | 1.9 | 243 244 245 | 244,243,244 | 241,240,244 | 1.9.6.5.6.4 | 0.2 0.1 1.1 | 0.3,1.6.1.7 | 0.1,1.1,1.1 | 3.5,3.2,3.0 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 12.3 | 12.5 | 12.0 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 3H | 100 | 90 | 50 | 90 | ok | 7223 ROHAIZAN | 7111 AZHAR YUNUS | KLMFEP-33001 | 4000480722 | SC_PM_QTR_UPS_4000480722.pdf
BAS | 21/10/2022 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 31.5 38.4 | 34 45M | 50 | 50 | 266 | 266 | 0.0 | -0.0 | 0.0 | 249,249,249 | 249,249,251 | 240,240,240 | 1.5,3.8,6.0 | 0.3,0.8,1.4 | 0.0,0.0,0.3 | 0.3,0.8,1.4 | 5,12,22 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 13.6 | 13-6 | 13-6 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 190 | 100 | 100 | 50 | 100 | Good Condition. | 7223 ROHAIZAN | 7111 AZHAR YUNUS | KLMFEP-33001 | 4000493753 | SC_PM_QTR_UPS_4000493753.pdf
BNG | 19/10/2022 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 % | 33.2, 36.4 | 3h 48m | 50 | 50 | 260 | 266 | +0.0 | -0.0 | 0.0 | 230 249 253 | 249,249,254 | 239,239 240 | 2.7, 3.1, 3.8 | 0.6, 1.4, 0.9 | 0.0, 0.2, 0.0 | 5.6, 1.4, 1.8 | 9, 22,14 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 13.6 Volt | 13.6 Volt | 13.4 Volt | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 150 | 100 | 70 | 50 | 70 | Good Condition. | 7223 | 7111 | KLMFEP-33001 | 4000493756 | SC_PM_QTR_UPS_4000493756.pdf
HAH | 17/01/2022 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 36.6, 49.4 | 5h 32m | 50 | 50 | 271 | 271 | 0.0 | 0.0 | 0 | 247, 247, 239 | 248, 276, 239 | 239, 239, 239 | 1.11, 2.3, 2.7 | 0.3, 0.5, 0.6 | +0.0, -0.0, -0.1 | 0.3, 0.5, 0.6 | 5, 8, 9 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 12.6 | 12.6 | 12.8 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 160 | 100 | 80 | 50 | 150 | All equipment in good condition | 7222 | 7111 | KLMFEP-33001 | 4000446351 | SC_PM_QTR_UPS_4000446351.pdf
BED | 26/10/2022 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100% | 26.0C |  | 50 | 50 | +272 | -272 |  |  |  |  | 240,242,243 | 243,243,243 | 40,39,42 |  |  |  | 8.7, 8.7, na |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 13.2 | 13.6 | 13.8 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked |  | 100 | 20 | 50 | 20 | all equipment in good conditions | 11727 | 7111 | KLMFEP-33001 | 4000493765 | SC_PM_QTR_UPS_4000493765.pdf
HAH | 17/10/2022 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100% | 36 | 6J 20m | 50 | 50 | 271 | -271 | 000 | -000 | 0.0 | 237, 236, 239 | 238,236,239 | 239, 239, 240 | 1.4, 2.3, 2.7 | 0.3,0.5,0.6 | 0.0, 0.0, -0.1 | 0.3,0.5,0.6 | 5,8,9 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 12.5 | 12.6 | 12.5 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 180 | 100 | 90 | 50 | 90 |  | 7222 | 7111 | KLMFEP-33001 | 4000493769 | SC_PM_QTR_UPS_4000493769.pdf
oa | 25/10/2022 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 32.5 | 3h | 49.9 | 49.97 | 247 | 247 | 0.0 | 0.0 | 0.0 |  | 247, 246, 245 | 230, 230, 230 | 2.4, 3.1, 5.0 | 0.5, 0.6, 0.2 | 2.1, 2.8, 4.2 |  | 0.8, 0.9, 0.9 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 12.8 | 13.0 | 12.8 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, Battery Working LED illuminate and UPS change to BATTERY MODE. | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 180 | 100 | 90 | 50 | 180 | all equipment in good conditions | 11727 | 7111 | KLMFEP-33001 | 4000493787 | SC_PM_QTR_UPS_4000493787.pdf
TUN | 15/01/2023 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 24, 26 | 3.6h | 50 | 50 | 267.6 | 267.8 | 241.2 | 241.3 |  | 240, 239, 241 | 240, 239, 241 | 241, 241, 241 | 1.9, 7.9, 6.9 | 0.2, 1.7, 1.1 | 0.2, 1.9, 1.4 | 0.3, 1.0, 1.0 | 3.4, 14.3, 11.2 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 13.2 | 13.4 | 13.5 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 3h 6m | 100 | 1h 8m | 50 | 68 | All equipment module and battery in good condition. | 7110 | 7111 | KLMFEP-33001 | 4000509048 | SC_PM_QTR_UPS_4000509048.pdf
MAH | 16/10/2022 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 3h | 2h 16m | 50 | 50 | 271 | 271 | 0.0 | 0.7 | 0.0 | 255, 254, 253 | 255, 256, 256 | 239, 239, 239 | 3.2, 6.3, 7.6 | 0.7, 1.5, 1.8 | 0.0, 0.3, 0.5 | 0.7, 1.5, 0.8 | 11, 23, 27 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 12.6 | 12.5 | 12.7 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 160 | 100 | 80 | 50 | 60 |  | 7222 | 7111 | KLMFEP-33001 | 4000493791 | SC_PM_QTR_UPS_4000493791.pdf
TUN | 15/10/2022 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 33 | 3h | 50 | 80 | 241 | 242 | 0.2 | 0.1 | 1.9 | 243, 244, 245 | 244, 243, 244 | 241, 240, 244 | 1.9, 6.5, 6.4 | 0.2, 0.1, 0.1 | 0.3, 1.6, 1.7 | 0.1, 1.1, 1.1 | 3.5, 3.2, 3.0 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 12.3 | 12.5 | 12.7 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 3h | 100 | 90 | 50 | 90 |  | 7222 | 7111 | KLMFEP-33001 | 4000509049 | SC_PM_QTR_UPS_4000509049.pdf
TSA | 24/10/2022 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 28, 33 | 3h 27m | 50 | 50 | 266 | 266 | 0.0 | 0.0 | 0.0 | 237, 238, 240 | 237, 238, 240 | 240, 239, 240 | 1.0, 4.8, 6.2 | 0.2, 1.3, 1.4 | -0.1, -0.1, -0.3 | 0.2, 1.2, 1.4 | 3, 19, 21 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 13.5 | 12.8 | 12.8 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 180 | 100 | 90 | 50 | 180 | 2 batery faulty and all equipment in good conditions | 11727 | 7111 | KLMFEP-33001 | 4000509052 | SC_PM_QTR_UPS_4000509052.pdf
TSA | 24/01/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 28.0, 33.0 | 3H 27M | 50 | 55 | 266 | 266 | 0 | 0 | 0.0 | 237, 238, 240 | 237, 238, 240 | 240,239,240 | 1.07,48,6.2 | 0.2, 1.3,1.4 | -0.1, -0.1,-0.3 | 0.2, 1.2,1.4 | 3,19,21 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 12.5 | 12.7 | 12.7 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 180 | 100 | 90 | 50 | 180 | Good Condition | 7223 | 7111 | KLMFEP-33001 | 4000509053 | SC_PM_QTR_UPS_4000509053.pdf
OCC | 25/01/2023 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 28 | 180 | 50 | 50 | 267 | 267 | 0.0 | 0.1 | 0 |  | 247,247,246 | 230,230,230 | 24,29,5.2 | 0.5,0.6,1.2 | 0.6,0.7,1.2 | 0.6,0.7,1.2 | 0.83, 0.89 0.93 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 12 | 12 | 12 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push |  | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 180 | 100 | 90 | 50 | 180 | GOOD CONDITION | 7223 | 7111 | KLMFEP-33001 | 4000509061 | SC_PM_QTR_UPS_4000509061.pdf
TKL | 22/01/2022 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 36.6, 42.6 | 5H 10M | 50 | 50 | 262 | 262 | 0.0 | 0.0 | 0.0 | 243,242, 244 | 243,242, 244 | 240, 240, 240 | 1.4,3.3,36 | 0.3, 0.7, 0.8 | 0.0, 0.1, -0.2 | 0.3, 0.8, 0.0 | 5, 12, 14 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 12.4 | 12.6 | 12.4 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 160 | 100 | 80 | 50 | 80 | OK | 7223 | 7111 | KLMFEP-33001 | 4000509067 | SC_PM_QTR_UPS_4000509067.pdf
MKU | 22/4/2022 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100% | 36.6, 42.6 | SH 10m | 60 | 60 | 262 | 262 | 0.0 | 0.0 | 0.00 | 243,242,244 | 243,242,244 | 240,240,240 | 1.4,3.3,3.6 | 0.3.0.7.0.78 | 0.0,0.1,-0.2 | 0.3,0.8,0.8 | 5,12,14 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 12.4 | 12.6 | 12.4 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 160 | 100 | 80 | 150 | 80 | ok | 7222 | 7111 | KLMFEP-33001 | 4000509068 | SC_PM_QTR_UPS_4000509068.pdf
MKU | 22/07/2022 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 31.2 37.9 | 4h 7m | 50 | 50 | 265 | 269 | 0 | 0 | 0.0 | 237,237,239 | 237,236,234 | 240,240,239 | 1.6,4.5,3.7 | 0.3,1.0,0.9 | 0.0, -0.2,-0.1 | 0.3,1.1,0.8 | 5,16,12 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 13.6 | 13.6 | 13.6 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, Battery Working LED illuminate and UPS change to BATTERY MODE. | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 240 | 100 | 100 | 50 | 400 | all equitment in good conditions | 11727 | 7111 | KLMFEP-33001 | 4000509069 | SC_PM_QTR_UPS_4000509069.pdf
MKU | 22/10/2022 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 31.3, 38.2 | 4H 01M | 50 | 50 | 268 | 268 | 0.0 | 0.0 | 0.0 | 234, 233, 235 | 234,233,235 | 240, 240, 240 | 1.6,4.7, 3.7 | 0.4, 1.0, 0.8 | 0.0, -0.2, -0.1 | 0.3, 1.1,0.8 | 5,15,14 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 13.4 | 13.5 | 13.6 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 240 | 100 | 100 | 80 | 100 | Good Condition | 7223 | 7111 | KLMFEP-33001 | 4000509070 | SC_PM_QTR_UPS_4000509070.pdf
HAH | 17/04/2022 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 | 37.9, 58.9 | 5h 26m | 50.06 | 50.00 | 271 | 271 | 00 | 00 | 0.0 | 238, 237, 240 | 238, 237, 24 | 239, 239, 240 | 1.3, 3.8, 2.6 | 0.3, 0.8, 0.6 | 0.0, 0.0, -0.1 | 0.3, 0.9, 0.6 | 4, 15, 9 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 13.4 | 13.4 | 13.4 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 150 | 100 | 80 | 50 | 80 | all equitment in good conditions | 11727 | 7111 | KLMFEP-33001 | 4000467082 | SC_PM_QTR_UPS_4000467082.pdf
Mku | 22/01/2023 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 31.3,34.2 | 4H | 50 | 50 | 269 | 268 | 0.0 | 0.0 | 0.0 | 234, 233, 235 | 234, 233, 235 | 240, 240, 240 | 1.6, 4.7, 3.7 | 0.4,1.1,0.8 | 0.0,-0.2,-0.1 | 0.3,1.1,0.8 | 5,15,14 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 13.4 | 13.5 | 13.5 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 200 | 100 | 100 | 50 | 100 |  | 7222 | 7111 | KLMFEP-33001 | 4000509072 | SC_PM_QTR_UPS_4000509072.pdf
MAH | 16/01/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | checked | 100 | 3H | 2H 16M | 50 | 50 | 271 | 271 | 0.0 | 0.7 |  | 255, 254, 236 | 255, 256, 256 | 239, 239, 239 | 2.2,6.3,7.6 | 0.7, 1.5, 1.3 | 0.0,-0.3,-0.5 | 0.7,1.5,1.8 | 11,23, 27 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 13.4 | 13.2 | 13.4 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 160 | 100 | 80 | 80 | 60 | An eaupment modem and battery in good artition. | 7110 | 7111 | KLMFEP-33001 | 4000509102 | SC_PM_QTR_UPS_4000509102.pdf
IBI | 18/01/2023 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 36 | 3h 10m | 60 | 50 | 286 | 286 | 0.0 | 0.0 | 0 | 250,250,254 | 250,250,254 | 239,239,240 | 3.2, 6.4, 7.1 | 0.4, 1.5, 2.0 | 0., -0.4, -0.2 | 0.7, 1.6, 1.9 | 11, 24, 30 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 12.8 | 12.9 | 12.7 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 140 | 100 | 95 | 50 | 95 | All equipment in good condition. | YARUL AZWAN | Engineer | KLMFEP-33001 | 4000509107 | SC_PM_QTR_UPS_4000509107.pdf
HAH | 17/01/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 24 | 2H 6M | 50 | 50 | 277 | 271 | 0.0 | 0.0 | 0 | 255, 254, 256 | 255,254,256 | 239, 239, 239 | 3.2, 6.3, 7.6 | 0.7,1.5, 1.8 | 0.0,-0.3,-0.5 | 0.7,1.6,1.8 | 11,19,20 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 12.5 | 12.6 | 12.6 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 160 | 100 | 80 | 50 | 60 | All annection cable with battery in secure procution. | 1110 | 7111 | KLMFEP-33001 | 4000509110 | SC_PM_QTR_UPS_4000509110.pdf
PFD | 26/01/2023 |  | Make sure safety precautions / procedures being followed as required. | Yes | Inform OCC before start any task. | Yes |  | Perform visual inspection and confirm all cable properly connected. | Yes | Confirm both of module is ON and inverter mode. | Yes | Using scroll arrow, scroll and record as below: | Yes | 100 | 28 |  | 50 | 50 | 272 | 272 | 0.0 | 0.0 |  |  | 240, 242, 243 | 243, 243, 243 | 4.0, 3.9, 4.2 |  |  |  | 5.7, 8.7, 8.7 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | Yes | Switching ON switch maintenance bypass in front of ups rack. | Yes | Confirm the Display panel is showing BYPASS MODE. | Yes | Switch OFF all battery breakers. | Yes | Switch OFF both of module using 2 finger push button ON/OFF. | Yes | Open screw and pull both of module to cleaning. | Yes | Open screws each battery bank and check the voltage. | Yes | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | Yes | 12.9 | 12.9 | 12.8 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | Yes | Maximum should not be more than 13.8V. | Yes | Check end-to-end batteries voltages. | Yes | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | Yes | After completed the cleaning, confirm all cablings. | Yes | Are secured and in the correct position. | Yes | Switch ON both of module using 2 finger push. | Yes | Button ON/OFF. | Yes | Normalized all battery breakers. | Yes | Switch OFF switch Maintenance bypass in front of UPS rack. | Yes | Set the ups to Inverter Mode by using command from module. | Yes | Confirm with OCC no alarm is activated on Scada. | Yes | Check and see is everything back to normal. | Yes | Before proceed this test, make sure battery level should be above 80% of load. | Yes | Confirm UPS in Inverter Mode and no alarm activated. | Yes | Turn OFF Main Switch Breaker for Main Incoming Supply. | Yes | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | Yes | Observe the UPS time remaining and battery percentage. | Yes | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | Yes |  | 100 | 20 | 50 | 20 | Good Condition | 7223 | 7111 | KLMFEP-33001 | 4000509113 | SC_PM_QTR_UPS_4000509113.pdf
CIT | 23/01/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 28.5, 35.0 | 6h 15m | 50 | 50 | 266 | 268 | 0.8 | 0.1 | 0 | 248, 247, 245 | 248, 2472/4400) | 240,240,231 (3000VA) | 1.1, 2.1, 4.1(43 A) | 0-2,0.4,0.9 | -0.1.10.0 -0.1 | 0.2 0.4 0.9 | 4 6 14 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 13.5 | 12.6 | 12.8 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 3h | 100 | 180 | 50 | 180 |  | 7223 | 7111 | KLMFEP-33001 | 4000509117 | SC_PM_QTR_UPS_4000509117.pdf
BNG | 19/01/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 33.1,36.4 | 3h 40m | 50 | 50 | 260 | 266 | 0.0 | 0.0 | 0 | 230, 249, 253 | 249, 249, 254 | 239, 239, 240 | 2.7, 3.1, 3.8 | 0.6, 1.4, 0.9 | 0.0, 0.2, 0.0 | 0.6, 1.4, 1.8 | 9, 22, 14 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 13.6 | 13.4 | 13.2 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 150 | 100 | 75 | 50 | 75 |  | 7222 | 7111 | KLMFEP-33001 | 4000509121 | SC_PM_QTR_UPS_4000509121.pdf
BAS | 21/04/23 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 31.5, 38.4 | 3h 45m. | 50 | 50 | 266 | 266 | 0.0 | 0 | 0 | 249, 249, 249 | 249, 249, 250 | 240, 240, 240 | 1.5, 3.8, 6.0 | 0.3, 0.0, 1.4 | 0.0, 0.0, 0.3 | 0.3, 0.0, 1.4 | 5, 12, 22 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 13.6 | 13.6 | 13.4 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 200 | 100 | 100 | 50 | 100 |  | 7110 | 7111 | KLMFEP-33001 | 4000530660 | SC_PM_QTR_UPS_4000530660.pdf
BFD | 25/04/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 28 |  | 50 | 50 | 272 | 272 | 0.0 | 0.0 |  |  | 240, 242, 243 | 243, 243, 243 | 40, 39, 42 |  |  |  | 7.7, 8.7, 8.7 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 12.9 | 12.7 | 12.8 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE |  | 100 | 20 | 50 | 20 |  | 7222 | 7111 | KLMFEP-33001 | 4000530675 | SC_PM_QTR_UPS_4000530675.pdf
HAH | 17/04/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 36.9, 43.0 | 4h | 49.97 | 50 | 267 | 267 | 0.00 | 0.1 | 0.0 | 239, 237, 239 | 238, 237, 240 | 239, 240, 240 | 1.6, 6.1, 2.6 | 0.4, 1.3, 0.7 | 0.0, 0.0. -0.1 | 0.4, 1.4, 0.6 | 5, 21, 9 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 12.8 | 13.2 | 13.1 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 150 | 100 | 150 | 50 | 180 min | all equipment | 11727 | 7111 | KLMFEP-33001 | 4000530679 | SC_PM_QTR_UPS_4000530679.pdf
1B1 | 18/04/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100% | 37.7, 44.7 | 2h 2m | 50 | 50 | 268 | 268 | 0.0 | 0.0 | 0.0 | 252, 253, 256 | 253, 253, 254 | 239, 239, 239 | 2.7, 6.2, 11.4 | 0.6, 1.4, 2.6 | 0.0, 0.5, 0.5 | 0.6, 1.4. 2.7 | 9, 22, 41 | 1 unit module ups Faulty | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 13.2 | 12.8 | 13 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 150 | 100 | 100 | 50 | 180 | all equitment in good conditions #1 unit bateri bank not good condition 1 unit module faulty | 11727 | 7111 | KLMFEP-33001 | 4000530683 | SC_PM_QTR_UPS_4000530683.pdf
MAH | 16/04/2023 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 | 35.8 | 2h | 50 | 50 | 267 | 267 | 0.0 | 0.0 | 0 | 245,244,246 | 245,245,245 | 239,240,239 | 2.7,6.7,9.6 | 0.6,1.5,2.2 | 0.0,-0.3,-0.5 | 0.6,1.6,2.3 | 10,23,37 | module 1 problem | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 12.3 | 12.2 | 12.5 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, Battery Working LED illuminate and UPS change to BATTERY MODE. | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 120 | 100 | 60 | 50 | 60 |  | 7223 | 7111 | KLMFEP-33001 | 4000530695 | SC_PM_QTR_UPS_4000530695.pdf
OCL | 26/04/2023 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 | 28 | 180 | 50 | 50 | 267 | 267 | 0.0 | 0.1 | 0.0 |  | 247,247,246 | 230,230,230 | 24,29,5.2 | 0.5,0.6,1.1 | 0.6,0.7,1.2 | 0.6,0.7,1.2 | 0.83,0.89,0.83 |  | Set the UPS to Maintenance Bypass Mode by using command from module. |  | Switching ON switch maintenance bypass in front of ups rack. |  | Confirm the Display panel is showing BYPASS MODE. |  | Switch OFF all battery breakers. |  | Switch OFF both of module using 2 finger push button ON/OFF. |  | Open screw and pull both of module to cleaning. |  | Open screws each battery bank and check the voltage. |  | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. |  | 12 | 12 | 12 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push |  | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 180 | 100 | 90 | 50 | 100 |  | 7222 | 7111 | KLMFEP-33001 | 4000530701 | SC_PM_QTR_UPS_4000530701.pdf
RIAN | 20/04/2023 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100% | 33.4 34.6 | 44 10m | 50 | 50 | 268 | -268 | 0 | 0 | 0.0 | 234, 234, 240 | 236 238, 236 | 240,240, 240 | 1.6, 4.5, 3.7 | 0.4, 1.0, 0.8 | 0.0, -0.2, -0.1 | 0.3, 1.1, 0.8 | 5, 15, 14 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 13.2 | 12.8 | 12.6 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 200 | 100 | 100 | 50 | 100 | all equipment in good conditions | 11727 | 7111 | KLMFEP-33001 | 4000530706 | SC_PM_QTR_UPS_4000530706.pdf
TSA | 24/04/2023 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100% | 28.0 ,33.0 | 34, 27 | 50 | 50 | +266 | -266 | +0.0 | -0.6 | 0 | 237, 238 ,240 | 237, 238, 260( 400) | 240, 259, 240 (3000VA) | 1.0,4.8, 6.2(43 A) | 0.2,1.2.1.7 | -0.1,-0.1, -0.3 | 0.2, 1.2, 1.4 | 3,19,21 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 125 | P7 | 12.7 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 180 | 100 | 90 | 50 | 180 | good Condition | 7110 | 7111 | KLMFEP-33001 | 4000530710 | SC_PM_QTR_UPS_4000530710.pdf
MAH | 16/07/2023 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 | 65 | 100 | 50 | 80 | 267 | 207 | 0.0 | 0.1 | 0.0 | 245, 245, 247 | 246, 246, 246 | 239, 239, 241 | 5.2, 5.6, 10.4 | 0.8, 1.4, 2.3 | 0.0, 0.3, 0.6 | 0.8, 1.4, 2.4 | 12, 25, 38 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of UPS rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | Yes | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on SCADA. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [5 empty] | one module operated | 7223 | 7111 | KLMFEP-33001 | 4000541165 | SC_PM_QTR_UPS_4000541165.pdf
TUN | 15/07/2023 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 |  |  | 50 | 50 | 247 | - 267 | 0.0 | 0.0 |  |  | 243, 242, 244 | 241, 241, 241 | 1.6, 8.1, 6.5 | 0.2, 1.6,1.1 | 0.4, 2.0, 1.6 | 0.0, 0.8, 1.6 | 0.8, 0.84, 0.75 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [5 empty] | good condition. | 7223 | 7111 | KLMFEP-33001 | 4000541175 | SC_PM_QTR_UPS_4000541175.pdf
AAS | 24/07/2023 |  | Make sure safety precautions / procedures being followed as required. | CHECKED | Inform OCC before start any task. | CHECKED |  | Perform visual inspection and confirm all cable properly connected. | CHECKED | Confirm both of module is ON and inverter mode. | CHECKED | Using scroll arrow, scroll and record as below: | CHECKED | 100 | 31.5, 38.4 | 3H 45M | 50 | 50 | 266 | -266 | 0.0 | 0.0 | 0.0 | 249, 249, 249 | 249, 249,260 | 240,240,240 | 1.5,3.8,6.0 | 0.3,0.8,1.4 | 0.0,0.0,0.2 | 1.3,0.8,1.4 | 5,12,32 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | CHECKED | Switching ON switch maintenance bypass in front of ups rack. | CHECKED | Confirm the Display panel is showing BYPASS MODE. | CHECKED | Switch OFF all battery breakers. | CHECKED | Switch OFF both of module using 2 finger push button ON/OFF. | CHECKED | Open screw and pull both of module to cleaning. | CHECKED | Open screws each battery bank and check the voltage. | CHECKED | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | CHECKED |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | CHECKED | Maximum should not be more than 13.8V. | CHECKED | Check end-to-end batteries voltages. | CHECKED | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | CHECKED | After completed the cleaning, confirm all cablings. | CHECKED | Are secured and in the correct position. | CHECKED | Switch ON both of module using 2 finger push. | CHECKED | Button ON/OFF. | CHECKED | Normalized all battery breakers. | CHECKED | Switch OFF switch Maintenance bypass in front of UPS rack. | CHECKED | Set the ups to Inverter Mode by using command from module. | CHECKED | Confirm with OCC no alarm is activated on Scada. | CHECKED | Check and see is everything back to normal. | CHECKED | Before proceed this test, make sure battery level should be above 80% of load. | CHECKED | Confirm UPS in Inverter Mode and no alarm activated. | CHECKED | Turn OFF Main Switch Breaker for Main Incoming Supply. | CHECKED | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | CHECKED | Observe the UPS time remaining and battery percentage. | CHECKED | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | CHECKED | [6 empty] | 7222 | 7111 | KLMFEP-33001 | 4000555036 | SC_PM_QTR_UPS_4000555036.pdf
BNG | 19/07/2023 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 | 46.0,50.9 | 54M | 50 | 50 | 266 | 264 | 0 | 0 | 0 | 246, 243, 246 | 245, 239, 240 | 240, 239, 240 | 2.7, 5.5, 3.5 | 0.6, 1.2, 0.6 | 0.1, -0.2, 0.1 | 0.6, 1.2, 0.8 | 12 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on SCADA. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [5 empty] | An equipment in good conditions | 7256 | 7111 | KLMFEP-33001 | 4000555042 | SC_PM_QTR_UPS_4000555042.pdf
ات | 23/07/2023 |  | Make sure safety precautions / procedures being followed as required. | CHECKED | Inform OCC before start any task. | CHECKED |  | Perform visual inspection and confirm all cable properly connected. | CHECKED | Confirm both of module is ON and inverter mode. | CHECKED | Using scroll arrow, scroll and record as below: | True | 110 | 37 | 2H 45M | 50 | 50 | 272 | 272 | 0.0 | 0.0 | 0.0 | 244 | 244,243,244 | 239,239,239 | 2.6,6.2,6.8 | 0.6,1.3,1.6 | 0.0,-0.1,-0.2 | 0.6, 1.2, 1.7 | 9,19,25 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | CHECKED | Switching ON switch maintenance bypass in front of UPS rack. | CHECKED | Confirm the Display panel is showing BYPASS MODE. | CHECKED | Switch OFF all battery breakers. | CHECKED | Switch OFF both of module using 2 finger push button ON/OFF. | CHECKED | Open screw and pull both of module to cleaning. | CHECKED | Open screws each battery bank and check the voltage. | CHECKED | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | CHECKED |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | CHECKED | Maximum should not be more than 13.8V. | CHECKED | Check end-to-end batteries voltages. | CHECKED | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | CHECKED | After completed the cleaning, confirm all cablings. | CHECKED | Are secured and in the correct position. | CHECKED | Switch ON both of module using 2 finger push. | CHECKED | Button ON/OFF. | CHECKED | Normalized all battery breakers. | CHECKED | Switch OFF switch Maintenance bypass in front of UPS rack. | CHECKED | Set the ups to Inverter Mode by using command from module. | CHECKED | Confirm with OCC no alarm is activated on SCADA. | CHECKED | Check and see is everything back to normal. | CHECKED | Before proceed this test, make sure battery level should be above 80% of load. | CHECKED | Confirm UPS in Inverter Mode and no alarm activated. | CHECKED | Turn OFF Main Switch Breaker for Main Incoming Supply. | CHECKED | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | CHECKED | Observe the UPS time remaining and battery percentage. | CHECKED | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | CHECKED | [6 empty] | 7222 | 7111 | KLMFEP-33001 | 4000555052 | SC_PM_QTR_UPS_4000555052.pdf
BFD | 26/07/2023 |  | Make sure safety precautions / procedures being followed as required. | CHECKED | Inform OCC before start any task. | CHECKED |  | Perform visual inspection and confirm all cable properly connected. | CHECKED | Confirm both of module is ON and inverter mode. | CHECKED | Using scroll arrow, scroll and record as below: | CHECKED | 100 | 28 |  | 50 | 50 | 272 | 271 | 0.0 | 0.0 |  |  | 240, 242, 243 | 243, 243, 243 | 40, 39, 42 |  |  |  | 5.7, 8.7, 8.7 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | CHECKED | Switching ON switch maintenance bypass in front of ups rack. | CHECKED | Confirm the Display panel is showing BYPASS MODE. | CHECKED | Switch OFF all battery breakers. | CHECKED | Switch OFF both of module using 2 finger push button ON/OFF. | CHECKED | Open screw and pull both of module to cleaning. | CHECKED | Open screws each battery bank and check the voltage. | CHECKED | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | CHECKED |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | CHECKED | Maximum should not be more than 13.8V. | CHECKED | Check end-to-end batteries voltages. | CHECKED | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | CHECKED | After completed the cleaning, confirm all cablings. | CHECKED | Are secured and in the correct position. | CHECKED | Switch ON both of module using 2 finger push. | CHECKED | Button ON/OFF. | CHECKED | Normalized all battery breakers. | CHECKED | Switch OFF switch Maintenance bypass in front of UPS rack. | CHECKED | Set the ups to Inverter Mode by using command from module. | CHECKED | Confirm with OCC no alarm is activated on Scada. | CHECKED | Check and see is everything back to normal. | CHECKED | Before proceed this test, make sure battery level should be above 80% of load. | UNCHECKED | Confirm UPS in Inverter Mode and no alarm activated. | UNCHECKED | Turn OFF Main Switch Breaker for Main Incoming Supply. | UNCHECKED | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | UNCHECKED | Observe the UPS time remaining and battery percentage. | UNCHECKED | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | [5 empty] | UPS error battery faulty do not backup tes, ups temporary in half in dition, dant have spare battery. | 7110 | 7111 | KLMFEP-33001 | 4000555059 | SC_PM_QTR_UPS_4000555059_1.pdf
BFO | 26/10/2023 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 | 28 |  | 50 | 50 | +272 | -27 | +0.0 | 0.0 |  |  | 240, 242, 243 | 243, 243, 243 | 40, 39, 42 |  |  |  | 5.7, 8.7, 8.7 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked |  |  | After completed the cleaning, confirm all cablings Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on SCADA. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | unchecked | Confirm UPS in Inverter Mode and no alarm activated. | unchecked | Turn OFF Main Switch Breaker for Main Incoming Supply. | unchecked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODЕ" | unchecked | Observe the UPS time remaining and battery percentage. | unchecked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | unchecked | [5 empty] | du not back up test, don't have spare batter, ups temporary in half condition, ups error battery faulty | 7248 | 7111 | KLMFEP-33001 | 4000555059 | SC_PM_QTR_UPS_4000555059.pdf
HAH | 17/07/2023 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 33.9, 39.9 | 4h 40m | 50 | 50 | 267 | 267 | 0.1 | 0.1 | 0 | 237, 236, 239 | 238, 236, 239 | 239, 239, 240 | 1.6, 3.6, 2.8 | 0.3, 0.7, 0.8 | 0.0, 0.0, 0.0 | 0.3, 0.8, 0.8 | 5, 13, 12 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of UPS rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on SCADA. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | [5 empty] | all equipment in good condition | 7256 | 7111 | KLMFEP-33001 | 4000555066 | SC_PM_QTR_UPS_4000555066.pdf
131 | 18/07/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 46.0, 50.9 | 54m | 50 | 50 | 266 | 266 | 0.0 | 0.0 | 0.0 | 246, 243, 246 | 245, 243, 247 | 240, 239, 240 | 2.7, 5.5, 3.5 | 0.6, 1.2, 0.7 | -0.1, -0.2, 0.1 | 0.6, 1.2, 0.8 | 10, 19, 12 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of UPS rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on SCADA. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, Battery Working LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | all equipment in good condition. | 7256 | 7111 | KLMFEP-33001 | 4000555072 | SC_PM_QTR_UPS_4000555072.pdf
OOO | 25/07/2023 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 28 | 180 | 80 | 50 | 267 | 267 | 0.0 | 0.1 | 0.0 | 347, 247, 244 | 247, 247, 246 | 230, 230, 230 | 2.4, 2.9, 1.1 | 0.6, 0.7, 1.2 | 0.6, 0.7, 1.2 | 0.6, 0.7, 1.2 | 0.83, 0.84, 0.83 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on SCADA. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | [5 empty] | - ups in good condition | 7110 | 7111 | KLMFEP-33001 | 4000555086 | SC_PM_QTR_UPS_4000555086.pdf
RAN | 20/07/2023 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100% | 33.8, 39.0 | 3h 49m | 50 | 50 | 267 | 267 | 0.0 | 0.1 | 0.0 | 242, 241, 242 | 241, 240, 242 | 239, 239, 240 | 2.1, 3.8, 5.3 | 0.5, 0.8, 1.2 | 0.0, 0.1, 0.1 | 0.5, 0.8, 1.3 | 7, 12, 19 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of UPS rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on SCADA. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | [6 empty] | 7222 | 7111 | KLMFEP-33001 | 4000555093 | SC_PM_QTR_UPS_4000555093.pdf
ISA | 24/07/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 32.7, 39.3 | 03h 55m | 50 | 50 | 266 | 206 | 0.0 | 0.0 | 0.0 | 235, 236, 237 | 240, 239, 240 | 1.4, 4.8, 5.1 | 0.3, 1.0, 1.2 | +0.0, -0.1, -0.3 | +0.0, -0.1, -0.3 | 0.3, 1.0, 1.2 | 5, 15, 18 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on SCADA. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, “Battery Working” LED illuminate and UPS change to “BATTERY MODE”. | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | All batery in good condition. connection cable and inficator module good condition | 7110 | 7111 | KLMFEP-33001 | 4000555099 | SC_PM_QTR_UPS_4000555099.pdf
BNG | 19/10/2023 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 40.3 , 43.7 | 50m | 50 | 50 | 266 | 266 | 0.0 | 0.0 | 0.0 | 252, 249, 252 | 251, 250, 253 | 240, 239, 240 | 3.0, 6.4, 3.7 | 0.7, 1.4, 0.8 | 0.1, 0.2, 0.1 | 0.7, 1.4, 0.9 | 10, 23, 13 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 13.4 | 13.2 | 13.4 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 50 | 100 | 49 | 48 | 49 | All in good condition | 19898 | 7111 | KLMFEP-33001 | 4000576113 | SC_PM_QTR_UPS_4000576113.pdf
CIT | 23/10/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 38 | 6h 05m | 50.03 | 50 | 266 | 268 | 0.0 | 0.1 | 0.0 | 250, 249, 250 | 250, 249, 251 | 239, 239, 239 | 1.3, 2.0, 3.9 | 0.2, 0.4, 0.9 | -0.1, -0.1, -0.2 | 0.3, 0.5, 0.9 | 4, 6, 14 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of UPS rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on SCADA. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | Time For both module not same Module 1 2h 25m and module 2 6h 5m | 7110 | 7111 | KLMFEP-33001 | 4000576119 | SC_PM_QTR_UPS_4000576119.pdf
HAH | 17/10/2023 |  | Make sure safety precautions / procedures being followed as required. | True | Inform OCC before start any task. | True |  | Perform visual inspection and confirm all cable properly connected. | True | Confirm both of module is ON and inverter mode. | True | Using scroll arrow, scroll and record as below: | True | 100% | 33.3/38.8 | 3h 53m | 50.5 | 50 | 267 | 267 | 0.01 | 0.1 | 0.0 | 238, 238, 240 | 236, 237, 240 | 239, 239, 246 | 1.5, 6.3, 3.4 | 0.4, 1.4, 0.7 | 1.0, 0.1, -0.1 | 0.4, 1.4, 0.7 | 6, 22, 10 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | True | Switching ON switch maintenance bypass in front of UPS rack. | True | Confirm the Display panel is showing BYPASS MODE. | True | Switch OFF all battery breakers. | True | Switch OFF both of module using 2 finger push button ON/OFF. | True | Open screw and pull both of module to cleaning. | True | Open screws each battery bank and check the voltage. | True | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | True |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | True | Maximum should not be more than 13.8V. | True | Check end-to-end batteries voltages. | True | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | True | After completed the cleaning, confirm all cablings. | True | Are secured and in the correct position. | True | Switch ON both of module using 2 finger push. | True | Button ON/OFF. | True | Normalized all battery breakers. | True | Switch OFF switch Maintenance bypass in front of UPS rack. | True | Set the ups to Inverter Mode by using command from module. | True | Confirm with OCC no alarm is activated on SCADA. | True | Check and see is everything back to normal. | True | Before proceed this test, make sure battery level should be above 80% of load. | True | Confirm UPS in Inverter Mode and no alarm activated. | True | Turn OFF Main Switch Breaker for Main Incoming Supply. | True | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | True | Observe the UPS time remaining and battery percentage. | True | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | True | [5 empty] | all equipment in good conditiong | 7256 | 7111 | KLMFEP-33001 | 4000576134 | SC_PM_QTR_UPS_4000576134.pdf
MAH | 16/10/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 % | 34.7, 41.6 | 2h 2m | 50.02 | 50 | +267 | -267 | +0.0 | -0.0 | 0.0 | 243, 242, 243 | 243, 243,244 | 239, 239, 239 | 3.4, 6.2, 10.4 | 0.7, 1.3, 2.2 | 0.0, -0.3, -0.7 | 0.8, 1.7, 2.5 | 11, 23, 37 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of UPS rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the UPS to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on SCADA. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | All good condition | 19920 | 7111 | KLMFEP-33001 | 4000576156 | SC_PM_QTR_UPS_4000576156.pdf
OCC | 25/10/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 26.6/32 | 180m | 50 | 50 | 267 | 268 | 0 | 0 | 0 | 247, 247, 244 | 247, 247, 245 | 230, 230.9, 230 | 2.8, 3.5, 4.3 | 2.3, 2.9, 3.4 | 0.6, 0.7, 1.1 | 0.6, 0.7, 1.2 | 0.03, 0.89, 0.84 |  | Set the UPS to Maintenance Bypass Mode by using command from module. |  | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. |  | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 13.50 | 13.30 | 13.40 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. |  | Button ON/OFF. |  | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the UPS to Inverter Mode by using command from module. |  | Confirm with OCC no alarm is activated on SCADA. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 3h 15 | 100 | 15 |  |  | ups good Condition | 7262 | 7111 | KLMFEP-33001 | 4000576167 | SC_PM_QTR_UPS_4000576167.pdf
RAN | 20/10/2023 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: |  | 100 |  | 3h 56m | 50.02 | 50 | 266 | 266 | 0.0 | 0.0 | 0.0 | 242, 241, 244 | 243, 241, 244 | 240, 240, 240 | 1.9, 3.7, 4.9 | 0.4, 0.8, 1.2 | 0.0, -0.2, -0.1 | 0.4, 0.8, 1.1 | 6, 13, 18 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. |  | Switch OFF both of module using 2 finger push button ON/OFF. |  | Open screw and pull both of module to cleaning. |  | Open screws each battery bank and check the voltage. |  | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. |  |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. |  | Maximum should not be more than 13.8V. |  | Check end-to-end batteries voltages. |  | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. |  | After completed the cleaning, confirm all cablings. |  | Are secured and in the correct position. |  | Switch ON both of module using 2 finger push. |  | Button ON/OFF. |  | Normalized all battery breakers. |  | Switch OFF switch Maintenance bypass in front of UPS rack. |  | Set the ups to Inverter Mode by using command from module. |  | Confirm with OCC no alarm is activated on Scada. |  | Check and see is everything back to normal. |  | Before proceed this test, make sure battery level should be above 80% of load. |  | Confirm UPS in Inverter Mode and no alarm activated. |  | Turn OFF Main Switch Breaker for Main Incoming Supply. |  | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". |  | Observe the UPS time remaining and battery percentage. |  | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | [6 empty] | All equipment in good condition | 20160 | 7111 | KLMFEP-33001 | 4000576174 | SC_PM_QTR_UPS_4000576174.pdf
TITIWANGSA | 24/10/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 33.0, 39.1 | 3h 48m | 50.04 | 50 | 266 | 266 | 0 | 0 | 0 | 234, 236, 237 | 234, 236, 237 | 240, 239, 240 | 1.2, 4.2, 5.4 | 0.3, 1.0, 1.2 | 0, 0, -0.3 | 0.3, 1.0, 1.2 | 4, 14, 20 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE |  | 100% |  |  | 3h 48m | All Good Condition | 7262 | 7111 | KLMFEP-33001 | 4000576188 | SC_PM_QTR_UPS_4000576188.pdf
BAS | 21/1/2024 |  | Make sure safety precautions / procedures being followed as required. | ✓ | Inform OCC before start any task. | ✓ |  | Perform visual inspection and confirm all cable properly connected. | ✓ | Confirm both of module is ON and inverter mode. | ✓ | Using scroll arrow, scroll and record as below: |  | 100% | 31.8, 38.3 | 3hrs 39 min | 50.0 | 50.00 | +266 | 266 | +0.0 | -0.0 | +0.0 | 249, 248, 252 | 249, 248, 252 | 240, 240, 241 | 1.5, 4.1, 6.0 | 0.3, 0.9, 1.4 | 0.0, -0.1, -0.2 | 0.3, 0.9, 1.5 | 5, 14, 23 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | ✓ | Switching ON switch maintenance bypass in front of ups rack. | ✓ | Confirm the Display panel is showing BYPASS MODE. | ✓ | Switch OFF all battery breakers. | ✓ | Switch OFF both of module using 2 finger push button ON/OFF. | ✓ | Open screw and pull both of module to cleaning. | ✓ | Open screws each battery bank and check the voltage. | ✓ | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | ✓ |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | ✓ | Maximum should not be more than 13.8V. | ✓ | Check end-to-end batteries voltages. | ✓ | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | ✓ | After completed the cleaning, confirm all cablings. | ✓ | Are secured and in the correct position. | ✓ | Switch ON both of module using 2 finger push. | ✓ | Button ON/OFF. | ✓ | Normalized all battery breakers. | ✓ | Switch OFF switch Maintenance bypass in front of UPS rack. | ✓ | Set the ups to Inverter Mode by using command from module. | ✓ | Confirm with OCC no alarm is activated on SCADA. | ✓ | Check and see is everything back to normal. | ✓ | Before proceed this test, make sure battery level should be above 80% of load. | ✓ | Confirm UPS in Inverter Mode and no alarm activated. | ✓ | Turn OFF Main Switch Breaker for Main Incoming Supply. | ✓ | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | ✓ | Observe the UPS time remaining and battery percentage. | ✓ | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | ✓ | [5 empty] | * Battery bank 1 and 2 (A01-040) need to be replaced. * Battery is damaged. * Battery can only cover 93% * Module P02 need to calibrate. | 20079 |  | KLMFEP-33001 | 4000597702 | SC_PM_QTR_UPS_4000597702.pdf
CIT | 23/01/2024 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 | 35.4, 42.5 | 24, 49 | 50.05 | 50.00 | 272 | 266 | 0.0 | 0.0 | 0.0 | 246, 246, 248 | 247, 246, 248 | 240, 240, 240 | 2.6, 5.7, 7.3 | 0.6, 1.4, 1.6 | 0.0, -0.1, -0.2 | 0.6, 1.3, 1.7 | 10, 18, 24 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. |  | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [5 empty] | All EQUIPMENT IN A GOOD CONDITION | 7248 | 7111 | KLMFEP-33001 | 4000597714 | SC_PM_QTR_UPS_4000597714.pdf
DCC | 26/1/24 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100% | 28°C |  | 50 H2 | 50 Hz | +272 | -272 | +0.0 | 0.0 |  |  | 2454 | 228 | 39.5A |  |  |  | 8-3 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. |  | Switch OFF all battery breakers. |  | Switch OFF both of module using 2 finger push button ON/OFF. |  | Open screw and pull both of module to cleaning. |  | Open screws each battery bank and check the voltage. |  | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. |  | Switch ON both of module using 2 finger push. |  | Button ON/OFF. |  | Normalized all battery breakers. |  | Switch OFF switch Maintenance bypass in front of UPS rack. |  | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. |  | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. |  | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to BATTERY MODE". |  | Observe the UPS time remaining and battery percentage. |  | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | [6 empty] | UPS in a good condition. I unit bateri voltage 25 | KARNA | AZHAR YUNUS | KLMFEP-33001 | 4000597742 | SC_PM_QTR_UPS_4000597742_1.pdf
DCC | 26/01/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: |  | 100 | 28 |  | 50 Hz | 50 Hz | 272 | 272 | 0.0 | 0.0 |  |  | 245 | 238 | 39.5 |  |  |  | 8.3 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. |  | Confirm the Display panel is showing BYPASS MODE. |  | Switch OFF all battery breakers. |  | Switch OFF both of module using 2 finger push button ON/OFF. |  | Open screw and pull both of module to cleaning. |  | Open screws each battery bank and check the voltage. |  | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. |  | 13.5 | 13.8 | 25 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. |  | Button ON/OFF. |  | Normalized all battery breakers. |  | Switch OFF switch Maintenance bypass in front of UPS rack. |  | Set the ups to Inverter Mode by using command from module. |  | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. |  | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. |  | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to BATTERY MODE". |  | Observe the UPS time remaining and battery percentage. |  | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | [6 empty] | Ups in a good condition. I unit bateri voltage 25V | 7262 | 7111 | KLMFEP-33001 | 4000597742 | SC_PM_QTR_UPS_4000597742.pdf
OCL | 25/04/2022 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 | 247,226,236 | 20553 | 49.9 | 49.6 | 261 | 267 | 268 | 288 | 1.3 |  | 244,243, 243 | 241, 241, 214 | 0.2, 2.1, 2.8 | 0.4,0.2, 2.4 | 0.5, 0.2, 0.5 | 0.5, 1.4, 2.6 | 7, 23, 36 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 13.4 | 13.4 | 13.4 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 20 | 100 | 50 | 50 | 20 | ok | 14952 | 7111 | KLMFEP-33001 | 4000467097 | SC_PM_QTR_UPS_4000467097.pdf
HAH | 17/01/2024 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100% | 35.7, 41.5 | 5h30m, 4h50m | 50.04, 50.04 | 50, 50 | +267 | -267 | +0.1 | -0.1 | 0.0 | 240, 237, 240 | 238, 237, 240 | 240, 239, 240 | 1.5, 3.5, 3.0 | 0.3, 0.8, 0.7 | 0.0, -0.0, -0.0 | 0.3, 0.8, 0.7 | 5, 13, 10 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of UPS rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on SCADA. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [5 empty] | * all battery fault except bank F. * condition both module in good condition. * battery take out. except bank F | 19898 | 7111 | KLMFEP-33001 | 4000597748 | SC_PM_QTR_UPS_4000597748.pdf
MAH | 16/01/2024 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 39.0, 45.8 | 2h 2m | 50 | 50 | 267 | 267 | 0 | 0.1 | 0.0 | 246, 246, 247 | 247, 247, 248 | 239, 239, 239 | 3.3, 6.3, 9.5 | 0.8, 1.6, 2.3 | 0, -0.2, -0.6 | 0.8, 1.5, 2.3 | 12, 22, 35 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of UPS rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. |  | Confirm UPS in Inverter Mode and no alarm activated. |  | Turn OFF Main Switch Breaker for Main Incoming Supply. |  | Confirm after a few seconds, alarm sounding, Battery Working LED illuminate and UPS change to BATTERY MODE. |  | Observe the UPS time remaining and battery percentage. |  | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | [6 empty] | 1. Only used 1 module because module power failure (module 1) 2. All batteries in good condition 3. Equipment in good condition. | 20826 | 7111 | KLMFEP-33001 | 4000597813 | SC_PM_QTR_UPS_4000597813.pdf
RAN | 20/01/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 31.1, 37.1 | 3h 50m | 50.08 | 50.00 | 266 | 266 | 0.0 | 0.0 | 0.0 | 243, 242, 245 | 242, 242, 245 | 240, 239, 240 | 2.0, 3.7, 5.3 | 0.4, 0.9, 1.2 | 0.0, -0.1, 0.1 | 0.5, 1.0, 1.2 | 7, 13, 18 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on SCADA. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | - Battery Bank 3 (EO1 - F40) need to be replaced - Battery 3 value is below 12V (EO1 - F40) | 20079 | 7111 | KLMFEP-33001 | 4000597864 | SC_PM_QTR_UPS_4000597864.pdf
TSA | 24/01/2024 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 33.0, 39.1 | 3h 48m | 50.04 | 50 | 266 | 266 | 0 | 0 | 0 | 234, 236, 237 | 234, 236, 237 | 240, 239, 240 | 1.2, 4.3, 5.4 | 0.3, 1.0, 1.2 | 0, 0, -0.3 | 0.3, 1.0, 1.2 | 4, 14, 20 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on SCADA. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | [5 empty] | All good condition | 7248 | 7111 | KLMFEP-33001 | 4000597870 | SC_PM_QTR_UPS_4000597870.pdf
RAN | 20/07/2024 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100% | 37.7, 43.7 | 3h 40m | 50.3 (50/60Hz) | 50 (50/60Hz) | +266 | -266 | +0.0 | -0.0 | 0.0 | 243, 243, 245 | 244, 243, 246 (400) | 240, 240, 240 (3000VA) | 2.2, 3.9, 5.5 (43 A) | 0.5, 0.9, 1.2 | 0.0, -0.2, -0.1 | 0.5, 0.9, 1.3 | 7, 15, 19 | BANK 2 & 3 BATERY DISMENTAL MCB F42 & F43 OFF | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on SCADA. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [5 empty] | Battery in good condition and all cable at bank properly connected | 20160 | 7223 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_11.pdf
KLS | 14/10/2022 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100% | 34.8, 41.6 | 03h 30m | 49.95 (50/60Hz) | 80.00(50/60Hz) | 267 | 268 | 0.0 | 0.0 | 0.0 | 255, 254, 256 | 254, 254, 255 (400) | 239, 240, 240 (3000VA) | 2.5, 5.9, 6.3 (43 A) | 0.6, 0.8, 1.4 | 10.0, -0.2, -0.2 | 0.5, 0.9, 1.5 | 8, 13, 22 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 12.6 | 12.7 | 12.6 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 100 | 100 | 60 | 80 | 120 | connection connector cable secure and system in good condition. | 7110 | 7111 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_1 (1).pdf
TUN | 15/01/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 30 | 70.4 | 50 | 50 | 267 | 267 | 0.0 | 0.0 | 0.0 | 55, 1, 34 | 244, 244, 246 | 241, 241, 241 | 1.9, 8.3, 6.5 | 0.2, 1.7, 1.2 | 0.4, 2.0, 1.6 | 0.3, 1.0, 1.0 | 84.4, 16.3, 15.9 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on SCADA. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | All equipment is in good condition | 19898 | 7111 | KLMFEP-33001 | 4000597877 | SC_PM_QTR_UPS_4000597877.pdf
OCC | 27/07/2024. |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100% |  | 629 | 49.93(50/60Hz) | 49.93 (50/60Hz) | +267 | 267 |  |  |  | 250, 249, 249 | 251, 249, 248 (400) | 231, 231, 231 (3000VA) | 13, 14, 17 (43 A) | 2.9, 3.0, 3.8 | 1.1, 1.3, 1.7 | 3.0, 3.4, 3.1 | 23, 25, 31 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on SCADA. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [5 empty] | Battery run test in good condition | 20826 | 7110 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_12.pdf
BAS | 21/04/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: |  | 100 | 33.1 | 03h 58m | 50.03 | 50.00 | 266 | 266 | 0 | 0.0 | 0.0 | 249, 248, 251 | 248, 249, 252 | 240, 239, 240 | 1.5, 3.4, 5.6 | 0.3, 0.8, 1.3 | 0.0, -0.1, -0.2 | 0.3, 0.8, 1.4 | 5, 12, 20 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, Battery Working LED illuminate and UPS change to BATTERY MODE. | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | All module and batteries in good condition. Only using bank 3, bank 1 and 2 temporary doesn't have batteries due expired batteries. | 19921 | 7111 | KLMFEP-33001 | 4000608011 | SC_PM_QTR_UPS_4000608011.pdf
KLS | 14/04/2023 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 36.7 | 1h 47m | 49.97 | 60 | 268 | 268 | 0.0 | 0.0 | 0 | 253, 253, 254 | 253, 253, 254 | 240, 239, 240 | 5.0.7.9.11.3 | 1.1 1.5 2.8 | -0.3, 0.5, 10.5 | 1.2,1.8 2.8 | 17,22,42 | I module problem | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 12.3 | 12.1 | 12.2 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 1h 42m | 100 | 60 | 50 | 40 | 1 Module Foil/problem | 7223 | 7111 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_1 (2).pdf
CHOW KIT | 23/04/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 28.2, 34.9 | 6h 9m | 50.4 | 50 | 266 | 268 | 0.0 | -0.1 | 0.0 | 249, 248, 250 | 249, 248, 250 | 240, 239, 239 | 1.3, 1.8, 3.9 | 0.3, 0.4, 0.9 | -0.1, -0.1, -0.2 | 0.3, 0.4, 0.9 | 5, 6, 14 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of UPS rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the UPS to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | (D01-D10) 1 battery faulty | 21048 | 7111 | KLMFEP-33001 | 4000608023 | SC_PM_QTR_UPS_4000608023.pdf
MAH | 16/07/2024 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 % | 35.2/42.0 | 2h 6min | 50.04 | 50 | 267 | -267 | 0.0 | 0.1 | 0.0 | 248, 247, 249 | 248, 248, 250 | 239, 239, 239 | 36, 6.0, 9. | 0.8, 1.5, 2.0 | -0.1 -0.3, -0.5 | 0.4, 1.5, 2.2 | 13, 23, 34 | Module 1 faulty | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | [5 empty] | All equipment in good condition | 9920 | 7256 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_13.pdf
Depoh | 26/04/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 28 |  | 50 | 50 | 272 | 272 |  |  | 0.0 | 246, 245, 247 | 246, 246, 246 | 240, 240, 240 | 37.7, 40.1, 36.7 | 7.7, 7.6, 8.1 | 8.7, 8.6, 8.8 | 96.4, 98.6, 102.3 |  | L: 54% | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on SCADA. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. |  | Confirm UPS in Inverter Mode and no alarm activated. |  | Turn OFF Main Switch Breaker for Main Incoming Supply. |  | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". |  | Observe the UPS time remaining and battery percentage. |  | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | [6 empty] | cant do battery run test because battery cannot support high load equipment | 21048 | 7111 | KLMFEP-33001 | 4000608031 | SC_PM_QTR_UPS_4000608031.pdf
OCC | 27/10/2023 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100% | 266/132 | 180m | 50 | 50 | +267 | 268 | + |  | 0 | 247, 247, 247 | 247, 247, 245 | 230,230.9, 230 | 2-3, 3-5, 4-3 | 2-3, 2-9, 3.4 | 6-6, 07, 1 | 0.6, 0.7, 1.2 | 0-03, 0-89, 0.84 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of UPS rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 13.3 | 13.3 | 13.4 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [5 empty] | UPS GOOD CONDITION | 7248 | 7111 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_1 (3).pdf
|  |  | Make sure safety precautions / procedures being followed as required. |  | Inform OCC before start any task. |  |  | Perform visual inspection and confirm all cable properly connected. |  | Confirm both of module is ON and inverter mode. |  | Using scroll arrow, scroll and record as below: | [20 empty] | Set the UPS to Maintenance Bypass Mode by using command from module. |  | Switching ON switch maintenance bypass in front of ups rack. |  | Confirm the Display panel is showing BYPASS MODE. |  | Switch OFF all battery breakers. |  | Switch OFF both of module using 2 finger push button ON/OFF. |  | Open screw and pull both of module to cleaning. |  | Open screws each battery bank and check the voltage. |  | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. |  |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. |  | Maximum should not be more than 13.8V. |  | Check end-to-end batteries voltages. |  | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. |  | After completed the cleaning, confirm all cablings. |  | Are secured and in the correct position. |  | Switch ON both of module using 2 finger push. |  | Button ON/OFF. |  | Normalized all battery breakers. |  | Switch OFF switch Maintenance bypass in front of UPS rack. |  | Set the ups to Inverter Mode by using command from module. |  | Confirm with OCC no alarm is activated on Scada. |  | Check and see is everything back to normal. |  | Before proceed this test, make sure battery level should be above 80% of load. |  | Confirm UPS in Inverter Mode and no alarm activated. |  | Turn OFF Main Switch Breaker for Main Incoming Supply. |  | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". |  | Observe the UPS time remaining and battery percentage. |  | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | [9 empty] | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_14.pdf
IBI | 18/04/2024 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 |  | 2h 0m | 50.04 | 50 | 269 | 269 | 0 | 0.0 | 0.0 | 251, 251, 255 | 251, 251, 252 | 240, 239, 239 | 2.9, 6.5, 10.8 | 0.7, 1.4, 2.6 | 0.0, -0.5,-0.4 | 0.7, 1.6, 2.5 | 11, 23, 38 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on SCADA. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | [5 empty] | Equipment is in good condition. Battery bank 2 no batery (C and D) | 20449 | 7111 | KLMFEP-33001 | 4000608042 | SC_PM_QTR_UPS_4000608042.pdf
Mku | 22/11/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 37.3 | 3h 58m | 50.04 | 50.00 | 268 | 268 | 0.0 | 0 | 0.0 | 238, 238, 239 | 238, 238, 239 | 239 239, 240 | 1.6, 5.3, 3.8 | 0.3, 1.2, 1.0 | 0.0, -0.3, -0.2 | 0.3, 1.2, 0.9 | 5, 19, 15 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | ALL EQUIPMENT IN GOOD CONDITION | 7248 | 7111 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_1 (4).pdf
MAH | 16/04/2024 |  | Make sure safety precautions / procedures being followed as required. | CHECKED | Inform OCC before start any task. | CHECKED |  | Perform visual inspection and confirm all cable properly connected. | CHECKED | Confirm both of module is ON and inverter mode. | CHECKED | Using scroll arrow, scroll and record as below: | CHECKED | 100 % |  | 02h13m | 50 | 50 | 267 | 267 | 0.1 | 0.1 | 0.0 | 247,246, 248 | 248, 248, 249 | 239, 239, 239 | 2.7,7.1,9.6 | 0.9, 1.5, 2.2 | +0.0,-0.3,-0.6 | 0.6, 1.5, 2.3 | 9,22,35 | One Module only (Module 2) | Set the UPS to Maintenance Bypass Mode by using command from module. | CHECKED | Switching ON switch maintenance bypass in front of ups rack. | CHECKED | Confirm the Display panel is showing BYPASS MODE. | CHECKED | Switch OFF all battery breakers. | CHECKED | Switch OFF both of module using 2 finger push button ON/OFF. | CHECKED | Open screw and pull both of module to cleaning. | CHECKED | Open screws each battery bank and check the voltage. | CHECKED | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | CHECKED |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | CHECKED | Maximum should not be more than 13.8V. | CHECKED | Check end-to-end batteries voltages. | CHECKED | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | CHECKED | After completed the cleaning, confirm all cablings. | CHECKED | Are secured and in the correct position. | CHECKED | Switch ON both of module using 2 finger push. | CHECKED | Button ON/OFF. | CHECKED | Normalized all battery breakers. | CHECKED | Switch OFF switch Maintenance bypass in front of UPS rack. | CHECKED | Set the UPS to Inverter Mode by using command from module. | CHECKED | Confirm with OCC no alarm is activated on SCADA. | CHECKED | Check and see is everything back to normal. | CHECKED | Before proceed this test, make sure battery level should be above 80% of load. | CHECKED | Confirm UPS in Inverter Mode and no alarm activated. | CHECKED | Turn OFF Main Switch Breaker for Main Incoming Supply. | CHECKED | Confirm after a few seconds, alarm sounding, Battery Working LED illuminate and UPS change to BATTERY MODE. | CHECKED | Observe the UPS time remaining and battery percentage. | CHECKED | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | CHECKED | [5 empty] | Bank 1 TRANSFER to HanG TUAH. Module 1 Problem.Equipment in good condition | 20449 | 7011 | KLMFEP-33001 | 4000608051 | SC_PM_QTR_UPS_4000608051.pdf
MKU | 22/04/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: |  | 100% | 225,23.8 | 3h 58m | 50.03,(50/60Hz) | 50.00,(50/60Hz) | +268 | -268 | 0 | -0.0 | 0.0 | 240,236,242 | 240,238,242,(400) | 240,239,241,(3000VA) | 1.6,5.1,4.3,(43 A) | 0.3,1.0,0.8 | 0.0,-0.4,-0.4 | 0.3,1.2,1.0 | 5,18,15 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of UPS rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the UPS to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | All batteries and module in good condition. | 19921 | 7111 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_1 (5).pdf
OCC | 25/04/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 % |  | 629 | 49.93 | 49.93 | +267 | -267 |  |  |  | 250, 249, 249 | 251, 249, 248 | 231, 231, 231 | 13, 14, 17 | 2.9, 3.0, 3.8 | 1.1, 1.3, 1.7 | 3.0, 3.4, 3.1 | 23, 25, 31 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of UPS rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | Battery run test in good condition. | 21048 | 7111 | KLMFEP-33001 | 4000608059 | SC_PM_QTR_UPS_4000608059.pdf
TSA | 24/04/2024 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: |  | 100% | 33.7, 40.1 | 3h 38min | 50.05(50/60Hz) | 50(50/60Hz) | +266 | -266 | + 0.0 | 0.0 | 0 | 236, 239, 241 | 236, 239 241 (400) | 240, 239, 240(3000VA) | 1.6, 5.5, 6.1 (43 A) | 0.3, 1.3, 1.3 | -0.1,-0.1-0.3 | 0.4, 1.2, 1.3 | 5, 20, 21 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of UPS rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on SCADA. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [5 empty] | -Hardware In good condition | 20079 | 7111 | KLMFEP-33001 | 4000608074 | SC_PM_QTR_UPS_4000608074.pdf
KLS | 14/10/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 35.2/43.6 | 3h 44m | 50 | 50 | +267 | -268 | +0.0 | -0.0 | 0.0 | 256, 255, 257 | 255, 255, 256 | 239, 238, 239 | 2.3, 3.8, 5.3 | 0.5, 0.9, 1.2 | 0.0, -0.2, 0.0 | 0.5, 0.9, 1.2 | 8, 13, 19 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | -Bank A, B, C temporary take out by Adc | 19922 | 7248 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_1 (7).pdf
MAH | 16/07/2022 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 | 3H | 2j 1bln | 50 | 50 | 271 | 271 | 0.0 | 0.7 | 0 | 255,254,256 | 255,256,256 | 239,237,239 | 3.2,6.3,7.6 | 0.7,15,1.8 | 0.0,-0.3,-0.5 | 0.7,1.5,0.8 | 11,23,27 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 12.8 | 12.6 | 12.6 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 160 | 100 | 80 | 50 | 60 | OK | 7223 ROHAIZAN | 7111 AZHAR YUNUS | KLMFEP-33001 | 4000480697 | SC_PM_QTR_UPS_4000480697.pdf
TUN | 15/04/2024 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100% | 30 | 70.4 | 50 | 50 | +267 | -267 | +0.0 | -0.0 | 0.0 | 55,1,34 | 244, 244, 246 | 241, 241, 241 | 1.9,8.3, 6.5 | 0.2, 1.7, 1.2 | 0.4, 2.0, 1.6 | 0.3, 1.0, 1.0 | 8.4, 16.3, 15.9 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on SCADA. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [5 empty] | all equipment are in good condition | 20449 | 7111 | KLMFEP-33001 | 4000608083 | SC_PM_QTR_UPS_4000608083.pdf
KLS | 14/01/2022 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 24 | 4h | 50 | 50 | +260 | -261 | +0.0 | -0.0 | 0.0 | 271 272 273 | 240 241 242 | 1.5 1.4 1.3 | 0.3 1.2 0.4 | 0.3 0.1 0.9 | 0.1 0.1 0.0 | 0.2 1.0 1.0 | 5,14,9 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 12.6 | 12.4 | 12.4 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. |  | 240 | 100 | 120 | 50 | 120 | OK | 7110 | 7111 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_1.pdf
OCC | 25/07/2024 | 4000615391 | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100% | 26.7 | 170m | 50 (50/60Hz) | 50(50/60Hz) | +266 | -267 | + 0 | 0 | 0 | 247, 247, 247 | 246, 247, 246 (400) | 230, 230, 230 (3000VA) | 2.3, 3.5, 4.3 (43 A) | 2.3, 2.9, 3.4 | 0.6, 0.7, 1.1 | 6.6, 07, 12 | 0.03, 0.89, 0.85 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. |  | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on SCADA. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | [5 empty] | ups In good condition | 22278 | 7222 | KLMFEP-33001 | 4000615391 | SC_PM_QTR_UPS_4000615391.pdf
KLS | 14/07/2022 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 40.1 | SH 49M | 14 | 50 | 20.7 | 24.8 | 0.0 | 0.0 | 0.0 | 248, 248, 247 | 249, 248, 248 | 230, 230, 231 | 5.3, 5.3, 10.3 | 1.2, 1.2, 2.3 | 0.3, 0.1, 0.4 | 1.2, 1.2, 2.3 | 19, 10, 25 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 12.6 Volt | 12.7 Volt | 12.5 Volt | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 100 | 100 | 60 | 50 | 120 |  | 7222 | 7111 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA (1).pdf
İBİ | 18/10/2024 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100% | 36.0,42.7 | 2h3M | 50.3 (50/60Hz) | 50 (50/60Hz) | 266 | 266 | 0.0 | 0.0 | 0.0 | 245, 245, 248 | 245, 245, 247 (400) | 239, 239, 239 (3000VA) | 2.9,7.1, 10.4 (43A) | 0.6, 1.4,2.4 | 0.0,-0.5 -0.5 | 0.6, 1.6.2.5 | 10, 25, 38 | Ups Only one inverter. | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | [5 empty] | All equipments in a good condition. | 22547 | 7262 | KLMFEP-33001 | 4000644023 | SC_PM_QTR_UPS_4000644023.pdf
muu | 22/07/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 31.3,38.2 | 4h 20m | 50 | 50 | 218 | 268 | 0.0 | 0.0 | 0.0 | 234,233,235 | 234,233,235 | 240,240,240 | 1.6,4.7,3.7 | 0.4,1.0,0.8 | 0.0,-0.2,-0.1 | 0.3,1.1,0.8 | 5,15,14 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [6 empty] | 7222 | 7111 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_2 (1).pdf
OCC | 27/04/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 26.6132 | 180m | 50 | 50 | 267 | 268 | 0 | 0 | 0 | 247,247,247 | 247,247,245 | 230,230.9,230 | 2.3,3.5,4.3 | 2.3,2.9,3.4 | 0.6,0.7,1.1 | 0.6,0.7,1.2 | 0.03,0.89,0.84 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 12 | 12 | 12 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. |  | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 180 | 100 | 90 | 50 | 180 |  | 7248 | 7111 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_2 (2).pdf
BNG | 19/10/2024 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 | 33.3,34.2 | 94,45 | 50.02 | 50 | 266 | 266 | 0.0 | 0.0 | 0.0 | 245, 243,246 | 245, 245, 246 | 240, 239 ,240 | 2.7, 6.1,3.9 | 0.6, 1.4, 0.9 | 0.1, 0.0, 0.0 | 0.6, 1.5,0.8 | 10, 22, 14 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on SCADA. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [5 empty] | All equipments in a good condition. | 22547 | 7262 | KLMFEP-33001 | 4000646740 | SC_PM_QTR_UPS_4000646740.pdf
CIT | 23/10/2024 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 % | 31.5 37.5 | 06h 19m | 50.04 (50/60Hz) | 50.00 (50/60Hz) | 266 | 268 | 0.0 | 0.1 | 0.0 | 299 ,248 ,250 | 299 ,247 ,250 (400) | 240 ,239, 239 (3000VA) | 1.2 ,1.9 ,3.6 (43 A) | 0.2, 0.5, 0.8 | -0.1 ,-0.1, -0.1 | 0.2 ,0.5, 0.9 | 4 ,6 ,13 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on SCADA. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, “Battery Working” LED illuminate and UPS change to “BATTERY MODE”. | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [5 empty] | replace for unit new battery-madule in good condition | 19925 | 7256 | KLMFEP-33001 | 4000646748 | SC_PM_QTR_UPS_4000646748.pdf
MKU | 22/10/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: |  | 100 | 32.5 | 04h 19m | 50.05 | 50.00 | + 268 | - 268 | + 0.0 | 0.0 | 0.0 | 237, 236, 238 | 237, 237, 239 | 240, 240, 239 | 1.6, 4.4, 3.7 | 0.3,1.1,0.8 | 0.0, 0.2, 0.1 | 0.4, 1.0, 1.8 | 5, 16.12 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, Battery Working LED illuminate and UPS change to BATTERY MODE. | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | All battery in good condition and perform very well. | 11727 | 7256 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_2 (3).pdf
HAH | 17/10/2021 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 % |  | 5H, 21m | 50 (50/60Hz) | 50 (50/60Hz) | +267 | -267 | +0.0 | 0.0 | 0.0 | 240, 239, 242 | 239, 238, 242(400) | 239, 240, 240 (3000VA) | 1.5.3.6, 2.9 (43 A) | 0.3,0.8,0.6 | 10.0,0.0,-0.1 | 0.3, 0.8, 0.6 | 5.12,9 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [5 empty] | All equipment in a good condition. | 20858 | 7262 | KLMFEP-33001 | 4000646788 | SC_PM_QTR_UPS_4000646788.pdf
KLS | 14/01/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 28,38.2 | 4H 30m | 50 | 50 | 268 | 263 | 0.00 | 0.0 | 0.0 | 234, 233, 235 | 236,334, 239 | 240, 240, 240 | 1.6, 4.7, 3.7 | 0.4, 1.0, 08 | 0.0,-0.2,-0.1 | 0.3,1.1, 0.8 | 5, 15, 14 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 12.8 | 12.6 | 12.7 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 200 | 100 | 100 | 50 | 100 | all equipment in good conditions | 11727 | 7111 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_2.pdf
MKU | 22/04/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 31.3, 38.2 | 4H | 50 | 50 | 268 | 268 | 0.0 | 0.0 | 0.0 | 234, 233, 235 | 234,233,235 | 240, 240, 240 | 1.6,4.7,3.1 | 0.4,1.0,0.3 | 0.0, -0.8,-0.1 | 0.3, 1.1, 0.8 | 5, 15, 14 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 13.4 | 13.5 | 13.5 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 200 | 100 | 100 | 150 | 100 |  | 7110 | 7111 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA (2).pdf
MAH | 16/10/2021 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: |  | 100% | 36.0.40.9 | 2 H 8M | 50 | 50 | +267 | -267 | +0 | -0 | 0 | 243, 241, 246 | 243, 242, 245 | 239, 239, 239 | 3.6.7.6.9.6 | 0.8.1.6, 2.2 | 0.1, 0.4, 0.6 | 0.4, 1.6, 2.2 | 12.23.34 | Module I unserviceable | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of UPS rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on SCADA. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [5 empty] | All equipment in good condition | 22547 | 7202 | KLMFEP-33001 | 4000646818 | SC_PM_QTR_UPS_4000646818.pdf
BFD | 26/7/2024 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | TRUE | 100% | 28% |  | 50 | 50 | 272 | 272 |  |  | 0.0 | 246, 245, 247 | 246, 246, 246 | 240, 240, 240 | 37.7, 40.1, 36.7 | 7.7, 7.6, 8.1 | 8.7, 8.6, 8.8 | 96.4, 98.6, 102.3 |  | L: 54°C | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on SCADA. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. |  | Confirm UPS in Inverter Mode and no alarm activated. |  | Turn OFF Main Switch Breaker for Main Incoming Supply. |  | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". |  | Observe the UPS time remaining and battery percentage. |  | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | [6 empty] | Cannot do battery run test due to battery cannot support high load equipment. | 19921, SYAZUAN | 7222, MOHD RAZIF | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_3 (1).pdf
RAN | 20/10/2024 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 | 34.1,40.3 | 3h 54m | 50.03 | 50.00 | 266 | 266 | 0.0 | 0.0 | 0.0 | 245 ,244 ,245 | 244 ,243, 246 | 239,239, 240 | 2.2 ,4.0 ,5.2 | 0.5, 0.9 ,1.2 | 0.0, 0.1, 0.1 | 0.5 ,0.8 ,1.2 | 8 ,13 ,19 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on SCADA. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [5 empty] | Breaker 2 and 3 not function, waiting for new battery | 11727 | 7256 | KLMFEP-33001 | 4000647410 | SC_PM_QTR_UPS_4000647410.pdf
Mku | 22/10/2023 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 |  | 4h 20m | 50 | 50 | 268 | 269 | 0 | 0 | 0 | 239,240,241 | 240,231,241 | 234,240,241 | 1.6,4.7,3.7 | 0.4,1.0,0.8 | 0.0,-0.2,-0.1 | 0.3,1.1,0.8 | 5,15,14 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | [5 empty] | -all equipment in good condition -all cable tigth and secure | 7119 | 7111 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_3.pdf
Tun | 15/10/2024 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 % | 21,23 |  | 50 | 50 | 267 | 267 | 267 | 268 | 0 | 55,1,34 | 242, 240, 243 | 241, 241, 241 | 0.2, 2.2, 1.8 | 0.1.0.4, 0.3 | 0.4, 2.0, 1.6 | 0.3, 1.0, 1.0 | 84.4,16.3, 15.9 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on SCADA. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [5 empty] | All in good condition | 19922 | 7248 | KLMFEP-33001 | 4000647425 | SC_PM_QTR_UPS_4000647425.pdf
LLS | 04/07/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 65 | 1h 45m | 50 | 50 | 268 | 268 | 0.0 | 0.0 | 0.0 | 254, 254, 255 | 254, 254, 255 | 240, 239, 239 | 4.8, 7.6, 11.5 | 1.1, 1.8, 2.0 | 0.3, 0.5, 0.4 | 1.1, 1.9, 2.7 | 17, 28, 45 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of UPS rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on SCADA. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | good condition | 7223 | 7111 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA (3).pdf
TUN | 15/07/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100% | 21.5 |  | 49.99 (50/60Hz) | 49.99 (50/60Hz) | +267.7 | -267.7 | +268.2 |  | 0.0 | 55,1,34 | 245.3,243.5,246.8,(400) | 241.5,241.3,241.3,(3000VA) | 1.8,8.0,6.9,(43 A) | 0.2,1.7,1.2 | 0.4,2.0,1.6 | 0.7,1.0,1.0 | 84.4,16.3,15.9 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the UPS to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on SCADA. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | All in good condition | 20450 | 7262 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_4.pdf
CIT | 23/1/25 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | true | 100 % | 27.7/33.8°C | 30.6h 17m | 50.1 (50/60Hz) | 50 (50/60Hz) | +266 | 268 | + 0.0 | -0.1 | 0.0 | 246,245,247 | 246, 245, 248 (400) | 239, 239, 239 (3000VA) | 1.1, 2.2, 3.6 (43 A) | 0.2,0.4, 0.8 | -1, 0.0, -0.1 | 0-3, 0-4 0.8 | 4,7,13 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [5 empty] | UPS in a good condition. | 22777 | 7222 | KLMFEP-33001 | 4000660367 | SC_PM_QTR_UPS_4000660367.pdf
BNG | 19/01/2025 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100% | 31.2/31.9 | 10h 10m | 50 | 50 | 266 | 266 | 0 | 0.0 | 0.0 | 249, 247, 251 | 249, 247, 251 | 240, 239, 240 | 2.8, 6.2, 3.6 | 0.6, 1.4, 1.0 | 0.2, 0.1, 0.1 | 0.6, 1.4, 0.8 | 10, 22, 14 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on SCADA. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | [5 empty] | All equipment in a good condition. | 22775 | 7110 | KLMFEP-33001 | 4000660374 | SC_PM_QTR_UPS_4000660374.pdf
KLS | 14/01/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100% | 34.2,40.9 | 1h 41m | 50.03 (50/60Hz) | 50 (50/60Hz) | +268 | -268 | +0.0 | -0.0 | 0.0 | 256,256,258 | 256,256,257,(400) | 239,239,240,(3000VA) | 4.9,7.6,11.8,(43 A) | 1.1,1.9,2.8 | 0.3,0.6,0.5 | 1.2,1.82.8 | 17,27,40 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the UPS to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on SCADA. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | All equipment is in good condition | 19898 | 7111 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA (4).pdf
BAS | 21/01/2025 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 % | 33.1, 39.8 | 04 h 3m | 50.03 (50/60Hz) | 50.00 (50/60Hz) | 266 | 266 | 0.0 | 0 | 0.0 A | 246, 247, 249 | 246, 246, 249 | 241, 230, 240 | 1.4, 3.1, 5.6 | 0.3, 0.7, 0.2 | +0.0, -0.2, -0.1 | 0.3, 0.8, 1.3 | 5, 12 19 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the UPS to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on SCADA. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | # UPS in a good condition | 2276 | 7222 | KLMFEP-33001 | 4000660989 | SC_PM_QTR_UPS_4000660989.pdf
IBI | 18/07/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: |  | 100% | 40.7,48.1 | 1h 51m | 50.04 (50/60Hz) | 50.00 (50/60Hz) | +266 | -266 | +0.0 | -0.0 | 0 | 242,242,245 | 242,242,244,(400) | 240,239,240(3000VA) | 2.9,7.0,10.7,(43 A) | 0.6,1.4,2.6 | +0.0,-0.5,-0.5 | 0.6,1.7,2.6 | 10,27,39 | Module I faulty | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of UPS rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the UPS to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on SCADA. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | UPS in good condition. | 20159 | 7256 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_5.pdf
KLS | 14/04/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100% | 34.1,40.9 | 1h 44m | 50.02 (50/60Hz) | 50.00 (50/60Hz) | +268 | -268 | +0.0 | -0.0 | 0.0 | 256,254,257 | 255,254,257,(400) | 239, 239, 240,(3000VA) | 5.0,8.1,12.1,(43 A) | 1.1,1.9,2.6 | -0.3,-0.6,-0.5 | 1.1,1.9,2.7 | 17,29,41 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of UPS rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | All equipment in good Condition | 20449 | 7111 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA (5).pdf
HAH | 17/07/7024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100% | 37.1,42.9 | 5h 15 min | 49.95 (50/60Hz) | 50 (50/60Hz) | +267 | -267 | +0.0 | -0.1 | 0.0 | 241,239,242 | 241,239,241,(400) | 239,239,240,(3000VA) | 1.6,3.5,3.4 (43 A) | 0.4,0.8,0.7 | 0.0,0.0,0.0 | 0.3,0.8,0.7 | 5,13,10 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the UPS to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on SCADA. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | All equipment in good condition. | 19920 | 7256 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_6.pdf
TSA | 24/01/2025 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | TRUE | 100 | 29.9, 35.9 | 3h 24m | 50.03 (50/60Hz) | 50 (50/60Hz) | 266 | 266 | 0.0 | 0.0 | 0 | 239, 241, 243 | 240, 241, 243 (400) | 240, 239 239 (3000VA) | 1.5, 5.5, 6.2 (43A) | 0.3, 1.2, 1.4 | -0.1, -0.2, -0.4 | 0.3, 1.1, 1.4 | 5%, 20%, 21% |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the UPS to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on SCADA. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | [5 empty] | UPS IN GOOD CONDITION | 22876 | 7110 | KLMFEP-33001 | 4000668040 | SC_PM_QTR_UPS_4000668040.pdf
RAN | 20/01/2025 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100% | 36.8, 43.0 | 3h57m | 50.6 (50/60Hz) | 50.0 (50/60Hz) | 266 | 266 | 0.0 | 0.0 | 0.0 | 241, 240, 243 | 241, 240, 243 (400) | 240, 240, 240 (3000VA) | 2.0, 4.1, 4.9 (43 A) | 0.5, 0.9, 1.2 | 0.0, -0.3 -0.1 | 0.5, 1.0, 1.2 | 7, 13, 17 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on SCADA. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | Only one bank (Bank A and Bank B) Other that, all equipment in a good conditions. | 22777 | 7222 | KLMFEP-33001 | 4000668095 | SC_PM_QTR_UPS_4000668095.pdf
MKU | 22/07/2024 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100% | 290,33.5 | 4h 25m | 49.98 (50/60Hz) | 50 (50/60Hz) | +26.9 | -26.9 | +0.0 | -0.0 | 0.0 | 237,236,240 | 237,236,240,(400) | 239,240,240,(3000VA) | 1.45,4.5,3.5,(43 A) | 0.3,1.0,0.8 | 0.0,-0.2,-0.1 | 0.3,1.0,0.8 | 5,17,13 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | [5 empty] | All batteries in good condition. | 22153 | 7223 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA (6).pdf
CIT | 23/11/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100% | 30.2,34.5 | 6h 17m | 50.02 (50/60Hz) | 50.00 (50/60Hz) | 266 | -268 | 0 | -0.1 | 0.0 | 245,243,246 | 245,243,247,(400) | 240,239,239,(3000VA) | 1.2,2.0,3.9,(43 A) | 0.2,0.5,0.9 | -0.1,-0.1,-0.1 | 0.3,0.4,0.9 | 4,7,14 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of UPS rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | ALL EQUIPMENTS ARE IN GOOD CONDITION | 21970 | 7223 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_7.pdf
MAH | 16/01/2025 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: |  | 100% | 36.3, 42.8 | 2h 5 min | 49.98 (50/60Hz) | 50 (50/60Hz) | 267 | 267 | 0.0 | 0.1 | 0.0 | 244, 243, 246 | 244, 244, 247 (400) | 239, 239, 239 (3000VA) | 2.7, 6.7, 9.6 (43A) | 0.8, 0.7, 2.3 | -0.1, -0.5, -0.5 | 0.8, 2.6, 2.2 | 12, 23, 34 | Bank A N/A | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of UPS rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on SCADA. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, 'Battery Working' LED illuminate and UPS change to 'BATTERY MODE'. | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | Bank A not available, All battery in good condition. | 22775 | 7110 | KLMFEP-33001 | 4000668132 | SC_PM_QTR_UPS_4000668132.pdf
CIT | 23/10/2022 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100% | 28.5, 35.0 | 06H 16m | 50 | 50 | 266 | 268 | 0.0 | -0.1 | 0.0 | 248 247 245 | 248, 247, 249 | 240, 240, 239 | 1.1, 2.1, 4.1 | 0.2, 0.4, 0.9 | -0,1,+0.0, -0.1 | 0.2, 0.4, 0.9 | 4, 6, 14 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 13-6 Volt | 12.7 Volt | 12.8 Volt | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 380 | 100 | 180 | 50 | 180 | all equipment in good conditions | 11727 | 7111 | KLMFEP-33001 | 4000493761 | SC_PM_QTR_UPS_4000493761.pdf
IBI | 18/01/2025 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: |  | 100% | 31.5, 35.2 | 24h 03m | 50.03 | 50 | 266 | 266 | +0.0 | -0.0 | 0.0 | 243, 243, 246 | 243, 243, 245 | 240, 240, 239 | 2.9, 6.8, 4.7 | 0.6, 1.5, 2.5 | 0.0, 0.6, 0.5 | 0.7, 1.7, 2.5 | 10, 25, 36 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on SCADA. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | trued | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | All equipment in a good condition | 22775 | 7110 | KLMFEP-33001 | 4000669108 | SC_PM_QTR_UPS_4000669108.pdf
TSA | 24/10/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 27.8,28.9 | 3h 30min | 49.95 (50/60Hz) | 50 (50/60Hz) | +266 | -266 | +00 | -00 | 0.00 | 241,240,243 | 241,240,242,(400) | 241,240,242,(3000VA) | 1.4,5.3,6.0,(43 A) | 0.3,1.1,1.3 | -0.1,-0.2,-0.4 | 0.3,1.1,1.4 | 5,20,21 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | All equipment are in good condition. | 20005 | 7248 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA (7).pdf
HAH | 17/01/2025 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 30.8, 34.7 | 4h 33 m | 50.04 (50/60Hz) | 50.00 (50/60Hz) | 26.7 | 26.7 | 0.0 | 0.0 | 0.0 | 235, 234, 236 | 235, 234, 239 (400) | 239, 240, 240 (3000VA) | 1.4, 3.8, 2.6 (43A) | 0.3, 0.8, 0.6 | 0.0, 0.01, -0.1 | 0.3, 0.9, 0.6 | 5, 13, 10 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | chetruecked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the UPS to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on SCADA. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working” LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | All battery and module working properly without any error. Bank 1 and 2 not available. Only bank 3 is available and in good condition | 22775 | 7110 | KLMFEP-33001 | 4000669114 | SC_PM_QTR_UPS_4000669114.pdf
BNG | 19/07/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: |  | 100% | 31.6,33.1 | 9h 51m | 50 (50/60Hz) | 50 (50/60Hz) | +266 | -266 | +0.0 | -0.0 | 0.0 | 245,244,247 | 246,245,247 (400) | 240,239,240 (3000VA) | 2.7,6.4,3.4 (43 A) | 0.6,1.5,0.8 | +0.1,+0.0,+0.0 | 0.6,1.5,1.9 | 10,23,13 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V and. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the UPS to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | all ementien in good condition | 20159 | 7256 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_8.pdf
KLS | 14/01/2025 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: |  | 100% |  | 3H 34M | 50.05 | 50 | 267 | 268 | 0 | 0 | 0.0 | 255, 253, 256 | 254, 256, 255 (400) | 239, 238, 239 (3000VA) | 2.3, 4.7, 5.8 (43 A) | 0.5, 0.9, 1.3 | 0.0,-0.2,0.0 | 0.5,1.0, 1.3 | 8, 16, 20 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of UPS rack. | checked | Confirm the Display panel is showing BYPASS MODE. |  | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V and Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the UPS to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on SCADA. | checked | Check and see is everything back to normal. | checked |  |  |  |  | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [5 empty] | The UPS only use one bank and one breaker. Everything is in good condition. This ups also use two module. | 22778 | 7110 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA (8).pdf
BFD DEPOT | 26/01/2025 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 |  | 50 | 50 | 50 | 268 | 268 | 0.0 | 0.0 | 0 | 242, 242, 245 | 242 | 240 | 38.5 | 8.6 | 3.7 | 8.9 | 30% | INLET: 27' OUTLET: 29 | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on SCADA. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [8 empty] | KLMFEP-33001 | 4000669120 | SC_PM_QTR_UPS_4000669120.pdf
TSA | 24/07/2024 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100% | 33.7,40.2 | 3h 30m | 50.04 (50/60Hz) | 50 (50/60Hz) | +266 | -266 | +0.00 | -0.00 | 0.0 | 237,239,240 | 237,239,24,(400) | 239,240,240,(3000VA) | 1.3,4.5,5.6,(43 A) | 0.3,1.1,1.3 | 0.0,0.0,-0.3 | 0.3,1.1,1.3 | 4,17,20 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 533.7 Volt | 533.6 Volt | 533.6 Volt | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V and. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | [5 empty] | Battery & Module in good condition. | 19921 | 7222 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA_9.pdf
MKU | 22/01/2025 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: |  | 100% | 28.6/35.1 | 04h 06 | 50.01 | 50 | +269 | -269 | + 0.0 | - 0.0 | 0.0 | 235, 234, 236 | 235, 234, 236 | 240, 239, 239 | 1.6, 4.4, 3.6 | 0.3,1.0,0.8 | 0.1,-0.2, -0.2 | 0.9,1.0, 0.9 | 5, 15, 13 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of UPS rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on SCADA. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [5 empty] | UPS in a good condition. | 22776 | 7222 | KLMFEP-33001 | 4000669552 | SC_PM_QTR_UPS_4000669552.pdf
KLS | 14/1/2025 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100% |  | 3h 34m | 50.05 | 50.00 | +267 | -268 | +0.0 | - 0.0 | 0.0 | 255, 253, 256 | 254,256,255 | 239,238, 239 | 2.3, 4.7, 5.8 | 0.5, 0.9, 1.3 | 0.0 -0.2.0.0 | 0.5,1.0, 1.3 | 8 16 20 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the UPS to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on SCADA. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [5 empty] | The UPS only use one bank and one breaker. Everything is in good condition. This up's also use two module. | 22778 | 7110 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA (9).pdf
kis | 14/04/2022 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | unchecked | 100% | 322 38-9 | 2h 30m | 50 (50/60Hz) | 50 (50/60Hz) | 271 | 271 | 0.0 | 00 | 00 | 248, 248, 248 | 798,249,148 (400) | 239 239 240 (3000VA) | 20.69.103 (43 A) | 04.1.4.2.4 | 0.0.-02, 0.5 | 0.5.1.4 2.0 | 7.23. 36 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 13.4 | 13.4 | 13.4 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, Battery Working LED illuminate and UPS change to BATTERY MODE. | checked | Observe the UPS time remaining and battery percentage. |  | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. |  | 150 | 100 | 80 | 80 | 50 | all equitment in good conditions | 11727 | 7111 | KLMFEP-33001 |  | SC_PM_NA_UPS_NA.pdf
RAN | 20/10/2022 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 32.7, 39.0 | 3h 48m | 49.9 | 50 | 266 | 266 | 0.0 | 0.1 | 0.0 | 242, 241, 242 | 241, 240, 241 | 239, 239, 240 | 2.1, 3.8, 5.3 | 0.5, 0.8, 1.2 | 0.0, 0.1, 0.2 | 0.5, 0.8, 1.2 | 7, 12, 19 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 13.3 Volt | 13.4 Volt | 12.6 Volt | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 180 | 100 | 90 | 50 | 90 | Good Condition. | 7223 | 7111 | KLMFEP-33001 | 4000493784 | SC_PM_QTR_UPS_4000493784.pdf
IBI | 18/10/2022 |  | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100 | 36 | 2H 18m | 50 | 50 | 236 | 236 | 00 | 0.0 | 000 | 250,250,251 | 250, 250, 252 | 239, 239, 240 | 3.2, 6.9, 7.7 | 0.7, 1.5, 2.0 | + 0.1, -0.4, -0.2 | 0.7, 1.6,1.9 | 11,2329 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked | 12.6 | 12.8 | 12.9 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on Scada. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | 3410 | 100 | 80 | 50 |  |  | 7222 | 7111 | KLMFEP-33001 | 4000493774 | SC_PM_QTR_UPS_4000493774.pdf
OCC | 25/10/2024 | 4000647402 | Make sure safety precautions / procedures being followed as required. | checked | Inform OCC before start any task. | checked |  | Perform visual inspection and confirm all cable properly connected. | checked | Confirm both of module is ON and inverter mode. | checked | Using scroll arrow, scroll and record as below: | checked | 100% | 21.0, 23.3 |  | 50.0 (50/60Hz) | 50.03 (50/60Hz) | + 267 | 267 | + 0.1 | 0.1 |  | 246, 245, 245 | 247, 246, 244 (400) | 231, 231, 231 (3000VA) | 11, 13.1, 19.3 (43 A) | 2.2, 2.7, 4.1 | 2.5, 3.0, 4.5 | 1.0, 1.1, 1.6 | 18.5,23,34.1 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | checked | Switching ON switch maintenance bypass in front of ups rack. | checked | Confirm the Display panel is showing BYPASS MODE. | checked | Switch OFF all battery breakers. | checked | Switch OFF both of module using 2 finger push button ON/OFF. | checked | Open screw and pull both of module to cleaning. | checked | Open screws each battery bank and check the voltage. | checked | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | checked |  |  |  | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | checked | Maximum should not be more than 13.8V. | checked | Check end-to-end batteries voltages. | checked | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | checked | After completed the cleaning, confirm all cablings. | checked | Are secured and in the correct position. | checked | Switch ON both of module using 2 finger push. | checked | Button ON/OFF. | checked | Normalized all battery breakers. | checked | Switch OFF switch Maintenance bypass in front of UPS rack. | checked | Set the ups to Inverter Mode by using command from module. | checked | Confirm with OCC no alarm is activated on SCADA. | checked | Check and see is everything back to normal. | checked | Before proceed this test, make sure battery level should be above 80% of load. | checked | Confirm UPS in Inverter Mode and no alarm activated. | checked | Turn OFF Main Switch Breaker for Main Incoming Supply. | checked | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | checked | Observe the UPS time remaining and battery percentage. | checked | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | checked | [5 empty] | All battery in good condition: | 22153 | 7222 | KLMFEP-33001 | 4000647402 | SC_PM_QTR_UPS_4000647402.pdf
RAN | 20/01/2023 |  | Make sure safety precautions / procedures being followed as required. | true | Inform OCC before start any task. | true |  | Perform visual inspection and confirm all cable properly connected. | true | Confirm both of module is ON and inverter mode. | true | Using scroll arrow, scroll and record as below: | true | 100 | 32.7, 39.0 | 34H 48m | 50 | 50 | 266 | 266 | 0.0 | 0.1 | 0.10 | 242, 241 242 | 241, 240, 242 | 239, 239, 240 | 211, 3.8, 5.3 | 0.5,0.8, 1.2 | 0.0, 0.1,0.2 | 0.5,0.8,1.2 | 7, 12, 19 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | true | Switching ON switch maintenance bypass in front of ups rack. | true | Confirm the Display panel is showing BYPASS MODE. | true | Switch OFF all battery breakers. | true | Switch OFF both of module using 2 finger push button ON/OFF. | true | Open screw and pull both of module to cleaning. | true | Open screws each battery bank and check the voltage. | true | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | true | 13.1 | 12.9 | 12.7 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | true | Maximum should not be more than 13.8V. | true | Check end-to-end batteries voltages. | true | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | true | After completed the cleaning, confirm all cablings. | true | Are secured and in the correct position. | true | Switch ON both of module using 2 finger push. | true | Button ON/OFF. | true | Normalized all battery breakers. | true | Switch OFF switch Maintenance bypass in front of UPS rack. | true | Set the ups to Inverter Mode by using command from module. | true | Confirm with OCC no alarm is activated on Scada. | true | Check and see is everything back to normal. | true | Before proceed this test, make sure battery level should be above 80% of load. | true | Confirm UPS in Inverter Mode and no alarm activated. | true | Turn OFF Main Switch Breaker for Main Incoming Supply. | true | Confirm after a few seconds, alarm sounding, Battery Working LED illuminate and UPS change to BATTERY MODE. | true | Observe the UPS time remaining and battery percentage. | true | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | true | 180 | 100 | 90 | 50 | 90 |  | 7222 | 7111 | KLMFEP-33001 | 4000509057 | SC_PM_QTR_UPS_4000509057.pdf
CIT | 23/04/2023 |  | Make sure safety precautions / procedures being followed as required. | TRUE | Inform OCC before start any task. | TRUE |  | Perform visual inspection and confirm all cable properly connected. | TRUE | Confirm both of module is ON and inverter mode. | TRUE | Using scroll arrow, scroll and record as below: | TRUE | 100 | 28.5, 35.0 | 6h 15m | 50 | 50 | +266 | -268 | +0.8 | -0.1 | 80 | 248, 247, 245 | 248, 247, 249 | 240, 240, 235 | 1.1, 2.1, 4.1 | 0.2, 0.4, 0.9 | -0.1, -10.0, -0.1 | 0.2, 0.4, 0.9 | 4, 6, 14 |  | Set the UPS to Maintenance Bypass Mode by using command from module. | TRUE | Switching ON switch maintenance bypass in front of ups rack. | TRUE | Confirm the Display panel is showing BYPASS MODE. | TRUE | Switch OFF all battery breakers. | TRUE | Switch OFF both of module using 2 finger push button ON/OFF. | TRUE | Open screw and pull both of module to cleaning. | TRUE | Open screws each battery bank and check the voltage. | TRUE | Wait for the electrolytic condensers on the power board to discharge (wait at least 15min) before proceed any maintenance work. | TRUE | 13.5 | 12.6 | 12.8 | Randomly check the voltages on the batteries. Ensure minimum voltage is read as 12V. | TRUE | Maximum should not be more than 13.8V. | TRUE | Check end-to-end batteries voltages. | TRUE | Do the cleaning on all the batteries. Confirm and ensure no cable is disconnected from any terminals. | TRUE | After completed the cleaning, confirm all cablings. | TRUE | Are secured and in the correct position. | TRUE | Switch ON both of module using 2 finger push. | TRUE | Button ON/OFF. | TRUE | Normalized all battery breakers. | TRUE | Switch OFF switch Maintenance bypass in front of UPS rack. | TRUE | Set the ups to Inverter Mode by using command from module. | TRUE | Confirm with OCC no alarm is activated on Scada. | TRUE | Check and see is everything back to normal. | TRUE | Before proceed this test, make sure battery level should be above 80% of load. | TRUE | Confirm UPS in Inverter Mode and no alarm activated. | TRUE | Turn OFF Main Switch Breaker for Main Incoming Supply. | TRUE | Confirm after a few seconds, alarm sounding, "Battery Working" LED illuminate and UPS change to "BATTERY MODE". | TRUE | Observe the UPS time remaining and battery percentage. | TRUE | Switch ON back Main Switch Breaker after UPS reaching 50% of battery level. | TRUE | 81 | 100 | 180 | 10 | 180 | Good Condition | 7110 | 7111 | KLMFEP-33001 | 4000530672 | SC_PM_QTR_UPS_4000530672.pdf

## notification
notification_no | notification_type | notification_date | maintenance_plant | target_date | maint_work_centre | reported_by | work_order_no | assigned_to | parent_work_order_no | system_status | user_status | functional_location | location | superior_equipment | equipment | coding | work_request | description | tasks | staff_details | comments | object_part_items | cause_items | activity_items | approval.date_closed | approval.supervisor_verification
12290095 | M7 | 27/05/2024 | 0805 | 19/04/2024 | WS20 | 10016079 | 4000608017 |  |  | NOPR NOPT ORAS | CLS ACK | PR AL-MRL-WS-STN-MRLBNG Station Bukit Bintang | WES Wayside Department |  | BNG-UPS Uninterruptable Power System | MRWSU001 I006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 19/04/2024 | SR 0752
12259383 | M7 | 19/03/2024 | 0805 | 18/01/2024 | WS20 | 10016079 | 4000597779 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLIBI Station Imbi | WES Wayside Department |  | IBI-UPS Uninterruptable Power System |  | MRWSU001 1006 Inspection - 3 Months Interval | PM Complete | [] | [] |  | [] | [] | [] | 18/01/2024 | 7111
12259343 | M7 | 19/03/2024 | 0805 | 19/01/2024 | WS20 | 10016079 | 4000597708 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLBNG Station Bukit Bintang | WES Wayside Department |  | BNG-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 10/01/2024 | 7111
12213771 | M7 | 19/12/2023 | 0805 | 15/10/2023 | WS20 | 10016079 | 4000576195 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLTUN Station Tun Sambanthan | WES Wayside Department |  | TUN-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 15/10/2023 | 7111
12213722 | M7 | 19/12/2023 | 0805 | 18/10/2023 | WS20 | 10016079 | 4000576144 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLIBI Station Imbi | WES Wayside Department |  | IBI-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 18/10/2023 | 7111
12213682 | M7 | 19/12/2023 | 0805 | 21/10/2023 | WS20 | 10016079 | 4000576104 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLBAS Station Bukit Nanas | WES Wayside Department |  | BAS-UPS Uninterruptable Power System | MRWSU001 1006 | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 21/10/2023 | 7111
12110775 | M7 | 08/05/2023 | 0805 | 19/04/2023 | WS20 | 10016079 | 4000530667 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLBNG Station Bukit Bintang | WES Wayside Department |  | BNG-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 19/04/2023 | 7111
[19 empty] | [] | [] |  | [] | [] | [] | 15/04/2023
[19 empty] | [] | [] |  | [] | [] | [] | 21/1/23
12290151 | M7 | 27/05/2024 | 0805 | 20/04/2024 | WS20 | 10016079 | 4000608067 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLRAN Station Raja Chulan | WES Wayside Department |  | RAN-UPS Uninterruptable Power System | MRWSU001 I006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 20/04/2024 | SR 0752
[19 empty] | [] | [] |  | [] | [] | []
[19 empty] | [] | [] |  | [] | [] | []
11948396 | M7 | 18/05/2022 | 0805 | 18/04/2022 | WS20 | 10016079 | 4000467087 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLIBI Station Imbi | WES Wayside Department |  | IBI-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 18/04/2022 | 7111
11948357 | M7 | 18/05/2022 | 0805 | 21/04/2022 | WS20 | 10016079 | 4000467064 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLBAS Station Bukit Nanas | WES Wayside Department |  | BAS-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 21/04/2022 | 7111
[19 empty] | [] | [] |  | [] | [] | []
12290115 | M7 | 27/05/2024 | 0805 | 17/04/2024 | WS20 | 10016079 | 4000608037 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLHAH Station Hang Tuah | WES Wayside Department |  | HAH-UPS Uninterruptable Power System | MRWSU001 I006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 17/04/2024 | 7223
11898819 | M7 | 21/01/2022 | 0805 | 15/01/2022 | WS20 | 10016079 | 4000446286 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLTUN Station Tun Sambanthan | WES Wayside Department |  | TUN-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 15/01/2022 | 7111
11898800 | M7 | 21/01/2022 | 0805 | 25/01/2022 | WS20 | 10016079 | 4000446335 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-BLD-MRLOCC Operation Control Centre | WES Wayside Department |  | OCC-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 25/01/2022 | 7111
11898794 | M7 | 21/01/2022 | 0805 | 16/01/2022 | WS20 | 10016079 | 4000446338 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLMAH Station Maharajalela | WES Wayside Department |  | MAH-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 16/01/2022 | 7111
11898782 | M7 | 21/01/2022 | 0805 | 18/01/2022 | WS20 | 10016079 | 4000446346 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLIBI Station Imbi | WES Wayside Department |  | IBI-UPS Uninterruptable Power System | MRWSU001 1006 | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 18/01/2022 | 7111
11898767 | M7 | 21/01/2022 | 0805 | 26/01/2022 | WS20 | 10016079 | 4000446356 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-BLD-MRLDCC Depot Control Centre | WES Wayside Department |  | DCC-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 26/01/2022 | 7111
11898758 | M7 | 21/01/2022 | 0805 | 23/01/2022 | WS20 | 10016079 | 4000446359 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLCIT Station Chow Kit | WES Wayside Department |  | CIT-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 23/01/2022 | 7111
11898753 | M7 | 21/01/2022 | 0805 | 19/01/2022 | WS20 | 10016079 | 4000446363 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLBNG Station Bukit Bintang | WES Wayside Department |  | BNG-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 19/01/2022 | 7111
11948363 | M7 | 18/05/2022 | 0805 | 19/04/2022 | WS20 | 10016079 | 4000467069 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLBNG Station Bukit Bintang | WES Wayside Department |  | BNG-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 19/04/2022 | 7111
11948367 | M7 | 18/05/2022 | 0805 | 23/04/2022 | WS20 | 10016079 | 4000467073 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLCIT Station Chow Kit | WES Wayside Department |  | CIT-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval |  | Quarterly Inspection for UPS System PM Complete | [] | [] |  | [] | [] | [] | 23/04/2022 | 7111
11948372 | M7 | 18/05/2022 | 0805 | 26/04/2022 | WS20 | 10016079 | 4000467077 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-BLD-MRLDCC Depot Control Centre | WES Wayside Department |  | DCC-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 26/04/2022 | 7111
11948413 | M7 | 18/05/2022 | 0805 | 16/04/2022 | WS20 | 10016079 | 4000467093 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLMAH Station Maharajalela | WES Wayside Department |  | MAH-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 16/04/2022 | 7111
11898745 | M7 | 21/01/2022 | 0805 | 21/01/2022 | WS20 | 10016079 | 4000446126 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLBAS Station Bukit Nanas | WES Wayside Department |  | BAS-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 21/01/2022 | 7111
11948424 | M7 | 18/05/2022 | 0805 | 20/04/2022 | WS20 | 10016079 | 4000467101 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLRAN Station Raja Chulan | WES Wayside Department |  | RAN-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 20/04/2022 | 7111
11948436 | M7 | 18/05/2022 | 0805 | 15/04/2022 | WS20 | 10016079 | 4000467110 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLTUN Station Tun Sambanthan | WES Wayside Department |  | TUN-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 15/04/2022 | 7111
11898812 | M7 | 21/01/2022 | 0805 | 24/01/2022 | WS20 | 10016079 | 4000446312 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLTSA Station Titiwangsa | WES Wayside Department |  | TSA-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 24/01/2022 | 7111
[19 empty] | [] | [] |  | [] | [] | []
[19 empty] | [] | [] |  | [] | [] | [] | 19/07/22
[19 empty] | [] | [] |  | [] | [] | [] | 23/07/2022 | SIG
[19 empty] | [] | [] |  | [] | [] | [] | 26/07/2022 | SIG & COMM 7111 *★ AZHAR YUNUS
11898807 | M7 | 21/01/2022 | 0805 | 20/01/2022 | WS20 | 10016079 | 4000446322 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLRAN Station Raja Chulan | WES Wayside Department |  | RAN-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 20/01/2022 | 7111
[19 empty] | [{'task': '', 'description': ''}] | [{'staff_id': '', 'name': '', 'plan_start_date_time': '', 'plan_end_date_time': '', 'total_hours': ''}] |  | [{'item': '', 'object_part': '', 'damage': ''}] | [{'item': '', 'cause': ''}] | [{'item': '', 'activity': ''}] | 17/07/2022
[19 empty] | [] | [] |  | [] | [] | []
[19 empty] | [] | [] |  | [] | [] | [] | 20/07/22 | Supervisor Verfication
[19 empty] | [] | [] |  | [] | [] | []
[19 empty] | [] | [] |  | [] | [] | [] | 24/04/22 | AZHAR 7111 YUNUS
[19 empty] | [] | [] |  | [] | [] | [] | 15/07/2022
[19 empty] | [] | [] |  | [] | [] | [] | 21/10/22
[19 empty] | [] | [] |  | [] | [] | []
11898775 | M7 | 21/01/2022 | 0805 | 17/01/2022 | WS20 | 10016079 | 4000446351 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLHAH Station Hang Tuah | WES Wayside Department |  | HAH-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 17/01/2022 | 7111
[19 empty] | [] | [] |  | [] | [] | [] | 26/10/22
[19 empty] | [] | [] |  | [] | [] | [] | 17/10/2022
[19 empty] | [] | [] |  | [] | [] | [] | 25/10/2022
[19 empty] | [] | [] |  | [] | [] | [] | 15/1/23
|  |  | 0805 Rapid Rail StarRail (Monorail) | [8 empty] | PRAL-MRL-WS-STN-MRLMAH Station Maharajalela | WES Wayside Department |  | MAH-UPS Uninterruptable Power System |  |  |  | [] | [] |  | [] | [] | [] | 16/10/2022 | true
[19 empty] | [] | [] |  | [] | [] | [] | 15/10/22 | Verified
[19 empty] | [] | [] |  | [] | [] | [] | 24/10/22
[19 empty] | [] | [] |  | [] | [] | [] | 24/01/23 | YES
[19 empty] | [] | [] |  | [] | [] | [] | 25/01/2023
[19 empty] | [] | [] |  | [] | [] | []
[19 empty] | [] | [] |  | [] | [] | [] | 22/04/22 | SIG & COMM ★ AZHAR YUNUS 7111
[19 empty] | [] | [] |  | [] | [] | [] | 22/07/2022 | Verified
[19 empty] | [] | [] |  | [] | [] | [] | 22/10/22
11948379 | M7 | 18/05/2022 | 0805 | 17/04/2022 | WS20 | 10016079 | 4000467082 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLHAH Station Hang Tuah | WES Wayside Department |  | HAH-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 17/04/2022 | 7111
[19 empty] | [] | [] |  | [] | [] | [] | 22/01/2023
[19 empty] | [] | [] |  | [] | [] | [] | 16/1/23
[19 empty] | [] | [] |  | [] | [] | [] | 18/01/2023
[12 empty] | PRAL-MRL-WS-STN-MRLHAH Station Hang Tuah | WES Wayside Department |  | HAH-UPS Uninterruptable Power System |  |  |  | [{'task': '', 'description': ''}] | [{'staff_id': '', 'name': '', 'plan_start_date_time': '', 'plan_end_date_time': '', 'total_hours': ''}] |  | [{'item': '', 'object_part': '', 'damage': ''}] | [{'item': '', 'cause': ''}] | [{'item': '', 'activity': ''}] | 17/01/2023 | Verified
[19 empty] | [] | [] |  | [] | [] | [] | 26/01/2023 | Yes
[19 empty] | [] | [] |  | [] | [] | [] | 23/01/23
[19 empty] | [] | [] |  | [] | [] | [] | 19/1/23 | TRUE
12110769 | M7 | 08/05/2023 | 0805 | 21/04/2023 | WS20 | 10016079 | 4000530660 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLBAS Station Bukit Nanas | WES Wayside Department |  | BAS-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 21/04/2023 | 7111
12110789 | M7 | 08/05/2023 | 0805 | 26/04/2023 | WS20 | 10016079 | 4000530675 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-BLD-MRLDCC Depot Control Centre | WES Wayside Department |  | DCC-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 25/04/2023 | 7111
12110794 | M7 | 08/05/2023 | 0805 | 17/04/2023 | WS20 | 10016079 | 4000530679 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLHAH Station Hang Tuah | WES Wayside Department |  | HAH-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 17/04/2023 | 7111
12110798 | M7 | 08/05/2023 | 0805 | 18/04/2023 | WS20 | I0016079 | 4000530683 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLIBI Station Imbi | WES Wayside Department |  | IBI-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 18/04/2023 | 7111
12110805 | M7 | 08/05/2023 | 0805 | 16/04/2023 | WS20 | 10016079 | 4000530695 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLMAH Station Maharajalela | WES Wayside Department |  | MAH-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 16/04/2023 | 7111
12110809 | M7 | 08/05/2023 | 0805 | 26/04/2023 | WS20 | 10016079 | 4000530701 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-BLD-MRLOCC Operation Control Centre | WES Wayside Department |  | OCC-UPS Uninterruptable Power System | MRWSU001 1006 | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 26/04/2023 | 7111
12110813 | M7 | 08/05/2023 | 0805 | 20/04/2023 | WS20 | 10016079 | 4000530706 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLRAN Station Raja Chulan | WES Wayside Department |  | RAN-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 20/04/2023 | 7111
12110817 | M7 | 08/05/2023 | 0805 | 24/04/2023 | WS20 | 10016079 | 4000530710 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLTSA Station Titiwangsa | WES Wayside Department |  | TSA-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 24/04/2023 | 7111
12131717 | M7 | 28/06/2023 | 0805 | 16/07/2023 | WS20 | 10016079 | 4000541165 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLMAH Station Maharajalela | WES Wayside Department |  | MAH-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 16/07/2023 | 7111
12131736 | M7 | 28/06/2023 | 0805 | 15/07/2023 | WS20 | 10016079 | 4000541175 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLTUN Station Tun Sambanthan | WES Wayside Department |  | TUN-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 15/07/2023 | 7111
12165908 | M7 | 08/09/2023 | 0805 | 21/07/2023 | WS20 | 10016079 | 4000555036 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLBAS Station Bukit Nanas | WES Wayside Department |  | BAS-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 21/07/2023 | 7111
12165916 | M7 | 08/09/2023 | 0805 | 19/07/2023 | WS20 | 10016079 | 4000555042 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLBNG Station Bukit Bintang | WES Wayside Department |  | BNG-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 19/07/2023 | 7111
12165924 | M7 | 08/09/2023 | 0805 | 23/07/2023 | WS20 | 10016079 | 4000555052 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLCIT Station Chow Kit | WES Wayside Department |  | CIT-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 23/07/23 | 7111
12165932 | M7 | 08/09/2023 | 0805 | 26/07/2023 | WS20 | 10016079 | 4000555059 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-BLD-MRLDCC Depot Control Centre | WES Wayside Department |  | DCC-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 26/07/2023 | 7111
12165932 | M7 | 08/09/2023 | 0805 | 26/10/2023 | WS20 | 10016079 | 4000555059 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-BLD-MRLDCC Depot Control Centre | WES Wayside Department |  | DCC-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 26/10/2023 | 7111
12165940 | M7 | 08/09/2023 | 0805 | 17/07/2023 | WS20 | 10016079 | 4000555066 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLHAH Station Hang Tuah | WES Wayside Department |  | HAH-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 17/07/2023 | 7111
12165948 | M7 | 08/09/2023 | 0805 | 18/07/2023 | WS20 | 10016079 | 4000555072 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLIBI Station Imbi | WES Wayside Department |  | IBI-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 18/07/2023 | 7111
12165972 | M7 | 08/09/2023 | 0805 | 25/07/2023 | WS20 | 10016079 | 4000555086 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-BLD-MRLOCC Operation Control Centre | WES Wayside Department |  | OCC-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 25/07/2023 | 7111
12165980 | M7 | 08/09/2023 | 0805 | 20/07/2023 | WS20 | 10016079 | 4000555093 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLRAN Station Raja Chulan | WES Wayside Department |  | RAN-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 20/07/2023 | 7111
12165989 | M7 | 08/09/2023 | 0805 | 24/07/2023 | WS20 | 10016079 | 4000555099 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLTSA Station Titiwangsa | WES Wayside Department |  | TSA-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System |  | [] | [] |  | [] | [] | [] | 24/07/2023 | 7111
12213690 | M7 | 19/12/2023 | 0805 | 19/10/2023 | WS20 | 10016079 | 4000576113 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLBNG Station Bukit Bintang | WES Wayside Department |  | BNG-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 19/10/2023 | 19/10/2023
12213698 | M7 | 19/12/2023 | 0805 | 23/10/2023 | WS20 | 10016079 | 4000576119 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLCIT Station Chow Kit | WES Wayside Department |  | CIT-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 23/10/2023 | 7111
12213714 | M7 | 19/12/2023 | 0805 | 17/10/2023 | WS20 | 10016079 | 4000576134 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLHAH Station Hang Tuah | WES Wayside Department |  | HAH-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 17/10/2023 | 7111
12213737 | M7 | 19/12/2023 | 0805 | 16/10/2023 | WS20 | 10016079 | 4000576156 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLMAH Station Maharajalela | WES Wayside Department |  | MAH-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 16/10/2023 | 7111
12213747 | M7 | 19/12/2023 | 0805 | 25/10/2023 | WS20 | 10016079 | 4000576167 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-BLD-MRLOCC Operation Control Centre | WES Wayside Department |  | OCC-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 25/10/2023 | 7111
12213755 | M7 | 19/12/2023 | 0805 | 20/10/2023 | WS20 | 10016079 | 4000576174 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLRAN Station Raja Chulan | WES Wayside Department |  | RAN-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 20/10/2023 | 7111
12213763 | M7 | 19/12/2023 | 0805 | 24/10/2023 | WS20 | 10016079 | 4000576188 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLTSA Station Titiwangsa | WES Wayside Department |  | TSA-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 24/10/2023 | 7111
12259333 | M7 | 19/03/2024 | 0805 | 21/01/2024 | WS20 | 10016079 | 4000597702 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLBAS Station Bukit Nanas | WES Wayside Department |  | BAS-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 21/01/24
12259357 | M7 | 19/03/2024 | 0805 | 23/01/2024 | WS20 | 10016079 | 4000597714 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLCIT Station Chow Kit | WES Wayside Department |  | CIT-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 23/01/2024 | 7111
12259366 | M7 | 19/03/2024 | 0805 | 26/01/2024 | WS20 | 10016079 | 4000597742 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-BLD-MRLDCC Depot Control Centre | WES Wayside Department | DCC-UPS Uninterruptable Power System |  | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 26/1/24 | SIC & COMM *7111 AZHAR YUNUS*
12259366 | M7 | 19/03/2024 | 0805 | 26/01/2024 | WS20 | 10016079 | 4000597742 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-BLD-MRLDCC Depot Control Centre | WES Wayside Department | DCC-UPS Uninterruptable Power System |  |  | MRWSU001 1006 Inspection - 3 Months Interval | PM Complete | [{'task': '', 'description': 'Quarterly Inspection for UPS System'}] | [] |  | [] | [] | [] | 26/01/2024 | 7111
11948420 | M7 | 18/05/2022 | 0805 | 25/04/2022 | WS20 | 10016079 | 4000467097 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-BLD-MRLOCC Operation Control Centre | WES Wayside Department |  | OCC-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 25/04/2022 | 7111
12259375 | M7 | 19/03/2024 | 0805 | 17/01/2024 | WS20 | 10016079 | 4000597748 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLHAH Station Hang Tuah | WES Wayside Department |  | HAH-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 17/01/2024 | 7111
12259399 | M7 | 19/03/2024 | 0805 | 16/01/2024 | WS20 | 10016079 | 4000597813 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLMAH Station Maharajalela | WES Wayside Department |  | MAH-UPS Uninterruptable Power System | MRWSU001 I006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 16/01/2024 | 7111
12259415 | M7 | 19/03/2024 | 0805 | 20/01/2024 | WS20 | 10016079 | 4000597864 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLRAN Station Raja Chulan | WES Wayside Department |  | RAN-UPS Uninterruptable Power System | MRWSU001 I006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 20/01/2024 | 7111
12259424 | M7 | 19/03/2024 | 0805 | 24/01/2024 | WS20 | 10016079 | 4000597870 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLTSA Station Titiwangsa | WES Wayside Department |  | TSA-UPS Uninterruptable Power System | MRWSU001 I006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 24/01/2024 | 7111
[13 empty] | RAN | [5 empty] | [] | [] |  | [] | [] | []
[19 empty] | [] | [] |  | [] | [] | []
12259432 | M7 | 19/03/2024 | 0805 | 15/01/2024 | WS20 | 10016079 | 4000597877 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLTUN Station Tun Sambanthan | WES Wayside Department |  | TUN-UPS Uninterruptable Power System | MRWSU001 I006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 15/01/2024 | 7111
[19 empty] | [] | [] |  | [] | [] | []
12290087 | M7 | 27/05/2024 | 0805 | 21/04/2024 | WS20 | 10016079 | 4000608011 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLBAS Station Bukit Nanas | WES Wayside Department |  | BAS-UPS Uninterruptable Power System | MRWSU001 I006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 21/04/2024 | SR 0752
[19 empty] | [] | [] |  | [] | [] | []
12290101 | M7 | 27/05/2024 | 0805 | 23/04/2024 | WS20 | 10016079 | 4000608023 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLCIT Station Chow Kit | WES Wayside Department |  | CIT-UPS Uninterruptable Power System | MRWSU001 I006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 23/04/2024 | 7110
[19 empty] | [] | [] |  | [] | [] | []
12290109 | M7 | 27/05/2024 | 0805 | 26/04/2024 | WS20 | 10016079 | 4000608031 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-BLD-MRLDCC Depot Control Centre | WES Wayside Department |  | DCC-UPS Uninterruptable Power System | MRWSU001 I006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System PM Complete | PM Complete | [] | [] |  | [] | [] | [] | 26/04/2024 | 7110
[19 empty] | [{'task': '', 'description': ''}] | [{'staff_id': '', 'name': '', 'plan_start_date_time': '', 'plan_end_date_time': '', 'total_hours': ''}] |  | [{'item': '', 'object_part': '', 'damage': ''}] | [{'item': '', 'cause': ''}] | [{'item': '', 'activity': ''}]
12312727 | M7 | 11/07/2024 | 0805 | 25/07/2024 | WS20 | 10016079 | 4000615391 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-BLD-MRLOCC Operation Control Centre | WES Wayside Department |  | OCC-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 25/7/24
12290122 | M7 | 27/05/2024 | 0805 | 18/04/2024 | WS20 | 10016079 | 4000608042 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLIBI Station Imbi | WES Wayside Department |  | IBI-UPS Uninterruptable Power System | MRWSU001 I006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 18/04/2024 | 7223
[19 empty] | [] | [] |  | [] | [] | []
12290136 | M7 | 27/05/2024 | 0805 | 16/04/2024 | WS20 | 10016079 | 4000608051 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLMAH Station Maharajalela | WES Wayside Department |  | MAH-UPS Uninterruptable Power System | MRWSU001 1006 INSPECTION -3 MONTHS INTERVAL | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 16/04/2024 | 7223
[19 empty] | [] | [] |  | [] | [] | []
12290144 | M7 | 27/05/2024 | 0805 | 25/04/2024 | WS20 | 10016079 | 4000608059 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-BLD-MRLOCC Operation Control Centre | WES Wayside Department |  | OCC-UPS Uninterruptable Power System | MRWSU001 I006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 25/04/2024 | 7110
12290158 | M7 | 27/05/2024 | 0805 | 24/04/2024 | WS20 | 10016079 | 4000608074 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLTSA Station Titiwangsa | WES Wayside Department |  | TSA-UPS Uninterruptable Power System | MRWSU001/1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 24/04/2024 | 7110
[19 empty] | [] | [] |  | [] | [] | []
[19 empty] | [] | [] |  | [] | [] | [] | 16/07/2022
12290164 | M7 | 27/05/2024 | 0805 | 15/04/2024 | WS20 | 10016079 | 4000608083 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLTUN Station Tun Sambanthan | WES Wayside Department |  | TUN-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 15/04/2024 | 7223
[19 empty] | [] | [] |  | [] | [] | []
12312727 | M7 | 11/07/2024 | 0805 | 25/07/2024 | WS20 | 10016079 | 4000615391 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-BLD-MRLOCC Operation Control Centre | WES Wayside Department |  | OCC-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 25/07/2024 | 7111
[19 empty] | [] | [] |  | [] | [] | []
12378397 | M7 | 03/12/2024 | 0805 | 18/10/2024 | WS20 | 10016079 | 4000644023 |  |  | NOPR NOPT ORAS OSTS | CLS ACK | PRAL-MRL-WS-STN-MRLIBI Station Imbi | WES Wayside Department |  | IBI-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM COMPLETE | [{'task': '0001', 'description': '1001'}] | [{'staff_id': '000012378397', 'name': '', 'plan_start_date_time': '00:00:00', 'plan_end_date_time': '00:00:00', 'total_hours': ''}] |  | [{'item': '0001', 'object_part': 'UPS', 'damage': ''}] | [{'item': '0001', 'cause': 'Scheduled maintenance'}] | [{'item': '0001', 'activity': 'Check / Inspect -'}]
[19 empty] | [] | [] |  | [] | [] | []
[19 empty] | [] | [] |  | [] | [] | []
12378367 | M7 | 03/12/2024 | 0805 | 19/10/2024 | WS20 | 10016079 | 4000646740 |  |  | NOPR NOPT ORAS OSTS | CLS ACK | PRAL-MRL-WS-STN-MRLBNG Station Bukit Bintang | WES Wayside Department |  | BNG-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM COMPLETE | [{'task': '0001', 'description': '1001'}] | [{'staff_id': '000012378367', 'name': '', 'plan_start_date_time': '00:00:00', 'plan_end_date_time': '00:00:00', 'total_hours': ''}] |  | [{'item': '0001', 'object_part': 'UPS', 'damage': ''}] | [{'item': '0001', 'cause': 'Scheduled maintenance'}] | [{'item': '0001', 'activity': 'Check / Inspect -'}]
12378374 | M7 | 03/12/2024 | 0805 | 23/10/2024 | WS20 | 10016079 | 4000646748 |  |  | NOPR NOPT ORAS OSTS | CLS ACK | PRAL-MRL-WS-STN-MRLCIT Station Chow Kit | WES Wayside Department |  | CIT-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM COMPLETE | [{'task': '0001', 'description': '1001'}] | [{'staff_id': '000012378374', 'name': '', 'plan_start_date_time': '00:00:00', 'plan_end_date_time': '00:00:00', 'total_hours': ''}] |  | [{'item': '0001', 'object_part': 'UPS', 'damage': ''}] | [{'item': '0001', 'cause': 'Scheduled maintenance'}] | [{'item': '0001', 'activity': 'Check/Inspect -'}]
[19 empty] | [] | [] |  | [] | [] | []
12378389 | M7 | 03/12/2024 | 0805 | 17/10/2024 | WS20 | 10016079 | 4000646788 |  |  | NOPR NOPT ORAS OSTS | CLS ACK | PRAL-MRL-WS-STN-MRLHAH Station Hang Tuah | WES Wayside Department |  | HAH-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM COMPLETE | [{'task': '0001', 'description': '1001'}] | [{'staff_id': '000012378389', 'name': '', 'plan_start_date_time': '00:00:00', 'plan_end_date_time': '00:00:00', 'total_hours': ''}] |  | [{'item': '0001', 'object_part': 'UPS', 'damage': ''}] | [{'item': '0001', 'cause': 'Scheduled maintenance'}] | [{'item': '0001', 'activity': 'Check / Inspect -'}]
[19 empty] | [] | [] |  | [] | [] | []
[19 empty] | [{'task': '', 'description': ''}] | [{'staff_id': '', 'name': '', 'plan_start_date_time': '', 'plan_end_date_time': '', 'total_hours': ''}] |  | [{'item': '', 'object_part': '', 'damage': ''}] | [{'item': '', 'cause': ''}] | [{'item': '', 'activity': ''}]
12378423 | M7 | 03/12/2024 | 0805 | 16/10/2024 | WS20 | 10016079 | 4000646818 |  |  | NOPR NOPT ORAS OSTS | CLS ACK | PRAL-MRL-WS-STN-MRLMAH Station Maharajalela | WES Wayside Department | MAH-UPS Uninterruptable Power System |  | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM COMPLETE | [{'task': '0001', 'description': '1001'}] | [{'staff_id': '000012378423', 'name': '', 'plan_start_date_time': '00:00:00', 'plan_end_date_time': '00:00:00', 'total_hours': ''}] |  | [{'item': '0001', 'object_part': 'UPS', 'damage': ''}] | [{'item': '0001', 'cause': 'Scheduled maintenance'}] | [{'item': '0001', 'activity': 'Check / Inspect -'}]
[19 empty] | [] | [] |  | [] | [] | []
12378437 | M7 | 03/12/2024 | 0805 | 20/10/2024 | WS20 | 10016079 | 4000647410 |  |  | NOPR NOPT ORAS OSTS | CLS ACK | PRAL-MRL-WS-STN-MRLRAN Station Raja Chulan | WES Wayside Department |  | RAN-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM COMPLETE | [{'task': '0001', 'description': '1001'}] | [{'staff_id': '000012378437', 'name': '', 'plan_start_date_time': '00:00:00', 'plan_end_date_time': '00:00:00', 'total_hours': ''}] |  | [{'item': '0001', 'object_part': 'UPS', 'damage': ''}] | [{'item': '0001', 'cause': 'Scheduled maintenance'}] | [{'item': '0001', 'activity': 'Check / Inspect -'}]
[19 empty] | [] | [] |  | [] | [] | []
12378452 | M7 | 03/12/2024 | 0805 | 15/10/2024 | WS20 | 10016079 | 4000647425 |  |  | NOPR NOPT ORAS OSTS | CLS ACK | PRAL-MRL-WS-STN-MRLTUN Station Tun Sambanthan | WES Wayside Department |  | TUN-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM COMPLETE | [{'task': '0001', 'description': '1001'}] | [{'staff_id': '000012378452', 'name': '', 'plan_start_date_time': '00:00:00', 'plan_end_date_time': '00:00:00', 'total_hours': ''}] |  | [{'item': '0001', 'object_part': 'UPS', 'damage': ''}] | [{'item': '0001', 'cause': 'Scheduled maintenance'}] | [{'item': '0001', 'activity': 'Check / Inspect -'}]
[19 empty] | [] | [] |  | [] | [] | []
[19 empty] | [] | [] |  | [] | [] | []
[7 empty] | 4000660367 |  |  |  |  | PRAL-MRL-WS-STN-MRLCIT Station Chow Kit | WES Wayside Department |  | CIT-UPS Uninterruptable Power System |  |  |  | [{'task': '0010', 'description': 'Quarterly Inspection for UPS System'}] | [{'staff_id': '10007222', 'name': 'MOHD RAZIF BIN RAZALI', 'plan_start_date_time': '23/01/2025 000000', 'plan_end_date_time': '23/01/2025 040000', 'total_hours': '4'}] | PM Completed | [] | [] | [] | 23/1/2025 | true
[19 empty] | [{'task': '', 'description': ''}] | [{'staff_id': '', 'name': '', 'plan_start_date_time': '', 'plan_end_date_time': '', 'total_hours': ''}] |  | [{'item': '', 'object_part': '', 'damage': ''}] | [{'item': '', 'cause': ''}] | [{'item': '', 'activity': ''}]
[19 empty] | [] | [] |  | [] | [] | []
[19 empty] | [{'task': '', 'description': ''}] | [{'staff_id': '', 'name': '', 'plan_start_date_time': '', 'plan_end_date_time': '', 'total_hours': ''}] |  | [{'item': '', 'object_part': '', 'damage': ''}] | [{'item': '', 'cause': ''}] | [{'item': '', 'activity': ''}]
[19 empty] | [] | [] |  | [] | [] | []
[19 empty] | [{'task': '', 'description': ''}] | [{'staff_id': '', 'name': '', 'plan_start_date_time': '', 'plan_end_date_time': '', 'total_hours': ''}] |  | [{'item': '', 'object_part': '', 'damage': ''}] | [{'item': '', 'cause': ''}] | [{'item': '', 'activity': ''}]
[19 empty] | [{'task': '', 'description': ''}] | [{'staff_id': '', 'name': '', 'plan_start_date_time': '', 'plan_end_date_time': '', 'total_hours': ''}] |  | [{'item': '', 'object_part': '', 'damage': ''}] | [{'item': '', 'cause': ''}] | [{'item': '', 'activity': ''}]
[19 empty] | [] | [] |  | [] | [] | []
[19 empty] | [] | [] |  | [] | [] | []
[19 empty] | [] | [] |  | [] | [] | []
[19 empty] | [{'task': '', 'description': ''}] | [{'staff_id': '', 'name': '', 'plan_start_date_time': '', 'plan_end_date_time': '', 'total_hours': ''}] |  | [{'item': '', 'object_part': '', 'damage': ''}] | [{'item': '', 'cause': ''}] | [{'item': '', 'activity': ''}]
[19 empty] | [] | [] |  | [] | [] | [] | 10/1/25
[19 empty] | [] | [] |  | [] | [] | [] | 23/10/22
[19 empty] | [{'task': '', 'description': ''}] | [{'staff_id': '', 'name': '', 'plan_start_date_time': '', 'plan_end_date_time': '', 'total_hours': ''}] |  | [{'item': '', 'object_part': '', 'damage': ''}] | [{'item': '', 'cause': ''}] | [{'item': '', 'activity': ''}]
[19 empty] | [] | [] |  | [] | [] | []
[19 empty] | [] | [] |  | [] | [] | [] | 17/1/25
[19 empty] | [] | [] |  | [] | [] | []
[19 empty] | [] | [] |  | [] | [] | []
[7 empty] | 4000669120 |  |  |  |  | PRAL-MRL-WS-BLD-MRLDCC Depot Control Centre | WES Wayside Department |  | DCC-UPS Uninterruptable Power System |  |  |  | [{'task': '0010', 'description': 'Quarterly Inspection for UPS System'}] | [{'staff_id': '10007110', 'name': 'SYAHRUL AZWAN BIN MOHD YUSOF', 'plan_start_date_time': '26/01/2025 00:00:00', 'plan_end_date_time': '26/01/2025 04:00:00', 'total_hours': '4'}] | PM COMPLETED | [{'item': '', 'object_part': 'UPS', 'damage': ''}] | [{'item': '', 'cause': 'Scheduled maintenance-', 'damage': ''}] | [{'item': '', 'activity': ''}] | 26/1/25 | SIG & COMM ★7110 YAHRUL AZXAN *
[19 empty] | [] | [] |  | [] | [] | []
[15 empty] | MKU-UPS Uninterruptable Power System |  |  |  | [] | [] |  | [] | [] | []
[19 empty] | [] | [] |  | [] | [] | []
[19 empty] | [] | [] |  | [] | [] | []
[19 empty] | [] | [] |  | [] | [] | [] | 20/10/22
|  |  | 0805 Rapid Rail StarRail (Monorail) | 18/10/2022 |  |  | 4000493774 |  |  |  |  | PRAL-MRL-WS-STN-MRLIBI Station Imbi | WES Wayside Department |  | IBI-UPS Uninterruptable Power System |  |  |  | [{'task': '0010', 'description': 'Quarterly Inspection for UPS System'}] | [] |  | [] | [] | [] | 18/10/2022 | Finished
12378429 | M7 | 03/12/2024 | 0805 | 25/10/2024 | WS20 | 10016079 | 4000647402 |  |  | NOPR NOPT ORAS OSTS | CLS ACK | PRAL-MRL-WS-BLD-MRLOCC Operation Control Centre | WES Wayside Department | OCC-UPS Uninterruptable Power System | OCC-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM COMPLETE | [{'task': '0001', 'description': '1001'}] | [{'staff_id': '000012378429', 'name': '', 'plan_start_date_time': '00:00:00', 'plan_end_date_time': '00:00:00', 'total_hours': ''}] |  | [{'item': '0001', 'object_part': 'UPS', 'damage': ''}] | [{'item': '0001', 'cause': 'Scheduled maintenance'}] | [{'item': '0001', 'activity': 'Check / Inspect -'}] | 26/10/2024 | 7111
[19 empty] | [] | [] |  | [] | [] | [] | 20/01/2023
12110781 | M7 | 08/05/2023 | 0805 | 23/04/2023 | WS20 | 10016079 | 4000530672 |  |  | NOPR NOPT ORAS | CLS ACK | PRAL-MRL-WS-STN-MRLCIT Station Chow Kit | WES Wayside Department |  | CIT-UPS Uninterruptable Power System | MRWSU001 1006 Inspection - 3 Months Interval | Quarterly Inspection for UPS System | PM Complete | [] | [] |  | [] | [] | [] | 23/04/2023 | 7111

## work_order
work_order_no | work_order_type | date_opened | requester | target_date | cost_centre | notification_no | notification_type | priority | assigned_to | parent_work_order_no | maint_act_type | work_centre | maintenance_plant | functional_location | location | superior_equipment | equipment | description | operations | materials | labour_details | comments | object_part | cause | damage | action | approval.date_closed | approval.supervisor_verification
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[6 empty] | 12259343 | M7 | [11 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[6 empty] | 12213682 | M7 | [11 empty] | [] | [] | []
[19 empty] | [] | [] | []
4000520523 | RAIL - Preventive Maintenance Order | 15/04/2023 |  | 15/04/2023 | PVM |  |  | 3-Medium | 8021131201 |  |  | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLTUN Station Tun Sambanthan | WES Wayside Department |  | TUN-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': ''}] | [] | [] | [5 empty] | 15/04/2023 | 7111
4000509125 | RAIL - Preventive Maintenance Order | 21/01/2023 |  | 21/01/2023 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLBAS Station Bukit Nanas | WES Wayside Department |  | BAS-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 21/01/2023 | 7111
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
4000668027 | RAIL - Preventive Maintenance Order | 15/01/2025 |  | 15/01/2025 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLTUN Station Tun Sambanthan | WES Wayside Department |  | TUN-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [{'staff_id': '10011727', 'name': 'ABDUL AZIM BIN NASIR', 'plan_start_date_time': '15/01/2025 00:00:00', 'plan_end_date_time': '15/01/2025 04:00:00', 'total_hours': '4'}] | PM COMPLETED | UPS | Scheduled maintenance- |  | Check / Inspect- | 15/01/2025 | 11727
[6 empty] | 11948396 | M7 |  |  |  |  | WS20 | 0805 | PRAL-MRL-WS-STN-MRLIBI Station Imbi | WES Wayside Department |  | IBI-UPS Uninterruptable Power System | PM Complete | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[6 empty] | 11898819 | M7 | [11 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[6 empty] | 11898758 | M7 | [11 empty] | [] | [] | []
[6 empty] | 11898753 | M7 | [11 empty] | [] | [] | []
[6 empty] | 11948363 | M7 | [11 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
4000467110 | [18 empty] | [] | [] | []
[19 empty] | [] | [] | []
4000480661 | RAIL - Preventive Maintenance Order | 21/07/2022 |  | 21/07/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLBAS Station Bukit Nanas | WES Wayside Department |  | BAS-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 21/07/2022 | 7111
4000480668 | RAIL - Preventive Maintenance Order | 19/07/2022 |  | 19/07/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLBNG Station Bukit Bintang | WES Wayside Department | BNG-UPS Uninterruptable Power System |  |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 19/7/22 | 7111 AZHAR YUNUS
4000480674 | RAIL - Preventive Maintenance Order | 23/07/2022 |  | 23/07/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLCIT Station Chow Kit | WES Wayside Department |  | CIT-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 23.7.22 | 7111 AZHAR YUNUS
4000480679 | RAIL - Preventive Maintenance Order | 26/07/2022 |  | 26/07/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-BLD-MRLDCC Depot Control Centre | WES Wayside Department | DCC-UPS Uninterruptable Power System |  |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 26.7.22 | 7111 AZHAR YUNUS
[19 empty] | [] | [] | []
4000480684 | RAIL - Preventive Maintenance Order | 17/07/2022 |  | 17/07/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLHAH Station Hang Tuah | WES Wayside Department |  | HAH-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [{'item_no': '', 'material_no': '', 'description': '', 'required_quantity': '', 'unit_of_measurement': ''}] | [{'staff_id': '', 'name': '', 'plan_start_date_time': '', 'plan_end_date_time': '', 'total_hours': ''}] | [5 empty] | 17/07/2022 | 7111
4000480689 | RAIL - Preventive Maintenance Order | 18/07/2022 |  | 18/07/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLIBI Station Imbi | WES Wayside Department |  | IBI-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 18/07/2022 | 7111 AZHAR YUNUS
4000480709 | RAIL - Preventive Maintenance Order | 20/07/2022 |  | 20/07/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLRAN Station Raja Chulan | WES Wayside Department |  | RAN-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 20/7/22 | 7111 AZHAR YUNUS
4000480715 | RAIL - Preventive Maintenance Order | 24/07/2022 |  | 24/07/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLTSA Station Titiwangsa | WES Wayside Department |  | TSA-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 24/7/22 | 7111 AZHAR YUNUS
4000480717 | RAIL - Preventive Maintenance Order | 24/04/2022 |  | 24/04/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLTSA Station Titiwangsa | WES Wayside Department |  | TSA-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 24/4/22 | 7111 AZHAR YUNUS
4000480722 | RAIL - Preventive Maintenance Order | 15/07/2022 |  | 15/07/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLTUN Station Tun Sambanthan | WES Wayside Department |  | TUN-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 15/07/2022 | 7111 AZHAR YUNUS
4000493753 | RAIL - Preventive Maintenance Order | 21/10/2022 |  | 21/10/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLBAS Station Bukit Nanas | WES Wayside Department |  | BAS-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 21/10/22 | 7111 AZHAR YUNUS
4000493756 | RAIL - Preventive Maintenance Order | 19/10/2022 |  | 19/10/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLBNG Station Bukit Bintang | WES Wayside Department |  | BNG-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 19/10/2022 | 7111
[19 empty] | [] | [] | []
4000493765 | RAIL - Preventive Maintenance Order | 26/10/2022 |  | 26/10/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-BLD-MRLDCC Depot Control Centre | WES Wayside Department |  | DCC-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 26/10/2022 | 7111
4000493769 | RAIL - Preventive Maintenance Order | 17/10/2022 |  | 17/10/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLHAH Station Hang Tuah | WES Wayside Department |  | HAH-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 17/10/2022 | 7111
4000493787 | RAIL - Preventive Maintenance Order | 25/10/2022 |  | 25/10/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-BLD-MRLOCC Operation Control Centre | WES Wayside Department |  | OCC-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 25/10/2022 | 7111
4000509048 | RAIL - Preventive Maintenance Order | 15/01/2023 |  | 15/01/2023 | 8021131201 |  |  | 2-High |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLTUN Station Tun Sambanthan | WES Wayside Department |  | TUN-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 15/01/2023 | 7111
4000493791 | RAIL - Preventive Maintenance Order | 16/10/2022 |  | 16/10/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLMAH Station Maharajalela | WES Wayside Department |  | MAH-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 16/10/2022 | 7111
4000509049 | RAIL - Preventive Maintenance Order | 15/10/2022 |  | 15/10/2022 | 8021131201 |  |  | 2-High |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLTUN Station Tun Sambanthan | WES Wayside Department |  | TUN-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 15/10/2022 | 7111
4000509052 | RAIL - Preventive Maintenance Order | 24/10/2022 |  | 24/10/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLTSA Station Titiwangsa | WES Wayside Department |  | TSA-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 24/10/2022 | 7111
4000509053 | RAIL - Preventive Maintenance Order | 24/01/2023 |  | 24/01/2023 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLTSA Station Titiwangsa | WES Wayside Department |  | TSA-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 24/01/23 | 7111
4000509061 | RAIL - Preventive Maintenance Order | 25/01/2023 |  | 25/01/2023 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-BLD-MRLOCC Operation Control Centre | WES Wayside Department |  | OCC-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 25/01/2023 | 7111
4000509067 | RAIL - Preventive Maintenance Order | 22/01/2022 |  | 22/01/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLMKU Station Medan Tuanku | WES Wayside Department |  | MKU-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 22/01/2022 | 7111
4000509068 | RAIL - Preventive Maintenance Order | 22/04/2022 |  | 22/04/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLMKU Station Medan Tuanku | WES Wayside Department |  | MKU-UPS Uninterruptable Power System S/n.: |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 22/04/2022 | 7111
4000509069 | RAIL - Preventive Maintenance Order | 22/07/2022 |  | 22/07/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLMKU Station Medan Tuanku | WES Wayside Department |  | MKU-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 22/07/2022 | 7111
4000509070 | RAIL - Preventive Maintenance Order | 22/10/2022 |  | 22/10/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLMKU Station Medan Tuanku | WES Wayside Department |  | MKU-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [6 empty] | 7111
[19 empty] | [] | [] | []
4000509072 | RAIL - Preventive Maintenance Order | 22/01/2023 |  | 22/01/2023 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLMKU Station Medan Tuanku | WES Wayside Department |  | MKU-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 22/01/2023 | 7111
4000509102 | RAIL - Preventive Maintenance Order | 16/01/2023 |  | 16/01/2023 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLMAH Station Maharajalela | WES Wayside Department |  | MAH-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 16/01/2023 | 7111
4000509107 | RAIL - Preventive Maintenance Order | 18/01/2023 |  | 18/01/2023 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLIBI Station Imbi | WES Wayside Department |  | IBI-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] |  | Cause |  |  |  | 18/01/2023 | 7111
4000509110 | RAIL - Preventive Maintenance Order | 17/01/2023 |  | 17/01/2023 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLHAH Station Hang Tuah | WES Wayside Department |  | HAH-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [{'item_no': '', 'material_no': '', 'description': '', 'required_quantity': '', 'unit_of_measurement': ''}] | [{'staff_id': '', 'name': '', 'plan_start_date_time': '', 'plan_end_date_time': '', 'total_hours': ''}] | [6 empty] | 7111
4000509113 | RAIL - Preventive Maintenance Order | 26/01/2023 |  | 26/01/2023 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-BLD-MRLDCC Depot Control Centre | WES Wayside Department |  | DCC-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 26/01/2023 | 7111
4000509117 | RAIL - Preventive Maintenance Order | 23/01/2023 |  | 23/01/2023 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLCIT Station Chow Kit | WES Wayside Department |  | CIT-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 23/01/2023 | 7111
4000509121 | RAIL - Preventive Maintenance Order | 19/01/2023 |  | 19/01/2023 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLBNG Station Bukit Bintang | WES Wayside Department |  | BNG-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 19/01/2023 | 7111
[19 empty] | [] | [] | []
[6 empty] | 12110789 | M7 | [11 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[6 empty] | 12110813 | M7 | [11 empty] | [] | [] | []
[6 empty] | 12110817 | [12 empty] | [] | [] | []
[7 empty] | M7 | [11 empty] | [] | [] | []
[7 empty] | M7 | [11 empty] | [] | [] | []
[19 empty] | [] | [] | []
[7 empty] | M7 |  |  |  |  | WS20 | 0805 | PRAL-MRL-WS-STN-MRLBNG Station Bukit Bintang | WES Wayside Department |  | BNG-UPS Uninterruptable Power System | PM Complete | [] | [] | []
[19 empty] | [] | [] | []
[13 empty] | 0805 | [5 empty] | [] | [] | []
[19 empty] | [] | [] | []
[6 empty] | 12165940 | M7 | [11 empty] | [] | [] | []
[6 empty] | 12165948 | M7 | [11 empty] | [] | [] | []
[6 empty] | 12165972 | M7 | [11 empty] | [] | [] | []
4000555093 |  |  |  | 20/07/2023 |  | 12165980 | M7 |  |  |  |  | WS20 | 0805 | PRAL-MRL-WS-STN-MRLRAN Station Raja Chulan | WES Wayside Department |  | RAN-UPS Uninterruptable Power System | PM Complete | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[6 empty] | 12213747 | M7 | [11 empty] | [] | [] | []
[6 empty] | 12213755 | [12 empty] | [] | [] | []
[6 empty] | 12213763 | M7 |  |  |  |  | WS20 | 0805 | PRAL-MRL-WS-STN-MRLTSA Station Titiwangsa | WES Wayside Department |  | TSA-UPS Uninterruptable Power System | PM Complete | [] | [] | []
[6 empty] | 12259333 | M7 | [11 empty] | [] | [] | []
[19 empty] | [] | [] | []
[6 empty] | 12259366 | M7 | [11 empty] | [] | [] | []
4000597742 | [5 empty] | 12259366 | M7 |  |  |  |  | WS20 | 0805 | PRAL-MRL-WS-BLD-MRLDCC Depot Control Centre | WES Wayside Department | DCC-UPS Uninterruptable Power System |  | Quarterly Inspection for UPS System, PM Complete | [] | [] | []
[6 empty] | 11948420 | M7 | [11 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
|  | 20/07/2024 | [6 empty] | TAUFIQ IRFAN | [5 empty] | RAN |  |  |  | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [{'operation_no': '', 'operation_text': ''}] | [{'item_no': '', 'material_no': '', 'description': '', 'required_quantity': '', 'unit_of_measurement': ''}] | [{'staff_id': '', 'name': '', 'plan_start_date_time': '', 'plan_end_date_time': '', 'total_hours': ''}]
4000615391 | RAIL - Preventive Maintenance Order | 25/07/2024 |  | 25/07/2024 | PVM |  |  | 3-Medium | 8021131201 |  |  | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-BLD-MRLOCC Operation Control Centre | WES Wayside Department |  | OCC-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
4000480697 | RAIL - Preventive Maintenance Order | 16/07/2022 |  | 16/07/2022 | 8021131201 |  |  | 3-Medium | 8021131201 |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLMAH Station Maharajalela | WES Wayside Department | MAH-UPS Uninterruptable Power System | MAH-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 16/7/22 | 7111 AZHAR YUNUS
[6 empty] | 12290164 | M7 | [6 empty] | PRAL-MRL-WS-STN-MRLTUN Station Tun Sambanthan | WES Wayside Department |  | TUN-UPS Uninterruptable Power System |  | [] | [] | []
[19 empty] | [] | [] | []
4000615391 | RAIL - Preventive Maintenance Order | 25/07/2024 |  | 25/07/2024 |  |  |  | 3-Medium | 8021131201 |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-BLD-MRLOCC Operation Control Centre | WES Wayside Department |  | OCC-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 25/7/2024
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [{'operation_no': '', 'operation_text': ''}] | [{'item_no': '', 'material_no': '', 'description': '', 'required_quantity': '', 'unit_of_measurement': ''}] | [{'staff_id': '', 'name': '', 'plan_start_date_time': '', 'plan_end_date_time': '', 'total_hours': ''}]
[6 empty] | 12378423 | M7 | [11 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
4000660367 | RAIL - Preventive Maintenance Order | 23/01/2025 |  | 23/01/2025 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLCIT Station Chow Kit | WES Wayside Department |  | CIT-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [{'staff_id': '10007222', 'name': 'MOHD RAZIF BIN RAZALI', 'plan_start_date_time': '23/01/2025 000000', 'plan_end_date_time': '23/01/2025 040000', 'total_hours': '4'}] | PM Completed | UPS | Scheduled maintenance- |  | Check / Inspect- | 23/1/2025 | 7222
4000660374 | RAIL - Preventive Maintenance Order | 19/01/2025 |  | 19/01/2025 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLBNG Station Bukit Bintang | WES Wayside Department |  | BNG-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [{'item_no': '', 'material_no': '', 'description': '', 'required_quantity': '', 'unit_of_measurement': ''}] | [{'staff_id': '10022775', 'name': 'MOHAMMAD ADIB AKMAL BIN MOHAMAD HALIT', 'plan_start_date_time': '19/01/2025 00:00:00', 'plan_end_date_time': '19/01/2025 04:00:00', 'total_hours': '4'}] | PM COMPLETED | UPS | Scheduled maintenance- |  | Check / Inspect- | 19/01/2025 | 7110
[19 empty] | [] | [] | []
4000660989 | RAIL - Preventive Maintenance Order | 21/01/2025 |  | 21/01/2025 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLBAS Station Bukit Nanas | WES Wayside Department | BAS-UPS Uninterruptable Power System |  |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [{'item_no': '', 'material_no': '', 'description': '', 'required_quantity': '', 'unit_of_measurement': ''}] | [{'staff_id': '10007222', 'name': 'MOHD RAZIF BIN RAZALI', 'plan_start_date_time': '21/01/2025 00:00:00', 'plan_end_date_time': '21/01/2025 04:00:00', 'total_hours': '4'}] | PM Completed | UPS | Scheduled maintenance- |  | Check / Inspect- | 21/01/2025 | 7222
[19 empty] | [] | [] | []
[19 empty] | [{'operation_no': '', 'operation_text': ''}] | [{'item_no': '', 'material_no': '', 'description': '', 'required_quantity': '', 'unit_of_measurement': ''}] | [{'staff_id': '', 'name': '', 'plan_start_date_time': '', 'plan_end_date_time': '', 'total_hours': ''}]
[19 empty] | [{'operation_no': '', 'operation_text': ''}] | [{'item_no': '', 'material_no': '', 'description': '', 'required_quantity': '', 'unit_of_measurement': ''}] | [{'staff_id': '', 'name': '', 'plan_start_date_time': '', 'plan_end_date_time': '', 'total_hours': ''}]
4000668040 | RAIL - Preventive Maintenance Order | 24/01/2025 |  | 24/01/2025 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLTSA Station Titiwangsa | WES Wayside Department |  | TSA-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [{'staff_id': '10007110', 'name': 'SYAHRUL AZWAN BIN MOHD YUSOF', 'plan_start_date_time': '24/01/2025 00:00:00', 'plan_end_date_time': '24/01/2025 04:00:00', 'total_hours': '4'}] | PM COMPLETED | UPS | Scheduled maintenance- |  |  | 24/01/2025 | 7110
4000668095 | RAIL - Preventive Maintenance Order | 20/01/2025 |  | 20/01/2025 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLRAN Station Raja Chulan | WES Wayside Department |  | RAN-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [{'staff_id': '10007222', 'name': 'MOHD RAZIF BIN RAZALI', 'plan_start_date_time': '20/01/2025 00:00:00', 'plan_end_date_time': '20/01/2025 04:00:00', 'total_hours': '4'}] | PM Completed | UPS | Scheduled maintenance- |  | Check / Inspect- | 20/01/2025 | 7222
[19 empty] | [] | [] | []
[19 empty] | [{'operation_no': '', 'operation_text': ''}] | [{'item_no': '', 'material_no': '', 'description': '', 'required_quantity': '', 'unit_of_measurement': ''}] | [{'staff_id': '', 'name': '', 'plan_start_date_time': '', 'plan_end_date_time': '', 'total_hours': ''}]
4000668132 | RAIL - Preventive Maintenance Order | 16/01/2025 |  | 16/01/2025 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLMAH Station Maharajalela | WES Wayside Department |  | MAH-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [{'staff_id': '10022775', 'name': 'MOHAMMAD ADIB AKMAL BIN MOHAMAD HALIT', 'plan_start_date_time': '15/01/2025 00:00:00', 'plan_end_date_time': '15/01/2025 04:00:00', 'total_hours': '4'}] | PM COMPLETED | UPS | Scheduled maintenance- |  | Check / Inspect- | 16/01/2025 | 11727
4000493761 | RAIL - Preventive Maintenance Order | 23/10/2022 |  | 23/10/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLCIT Station Chow Kit | WES Wayside Department |  | CIT-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 23/10/2022 | 7111
4000669108 | RAIL - Preventive Maintenance Order | 18/01/2025 |  | 18/01/2025 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLIBI Station Imbi | WES Wayside Department |  | IBI-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [{'item_no': '', 'material_no': '', 'description': '', 'required_quantity': '', 'unit_of_measurement': ''}] | [{'staff_id': '10022775', 'name': 'MOHAMMAD ADIB AKMAL BIN MOHAMAD HALIT', 'plan_start_date_time': '18/01/2025 00:00:00', 'plan_end_date_time': '18/01/2025 04:00:00', 'total_hours': '4'}] | PM COMPLETED |  |  |  |  | 18/01/2025 | 7110
[19 empty] | [] | [] | []
4000669114 | RAIL - Preventive Maintenance Order | 17/01/2025 |  | 17/01/2025 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLHAH Station Hang Tuah | WES Wayside Department |  | HAH-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [{'staff_id': '10022775', 'name': 'MOHAMMAD ADIB AKMAL BIN\nMOHAMAD HALIT', 'plan_start_date_time': '17/01/2025 00:00:00', 'plan_end_date_time': '17/01/2025 04:00:00', 'total_hours': '4'}] | PM COMPLETED | UPS | Scheduled maintenance- |  | Check / Inspect- | 17/01/2025 | 11727
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
4000669120 | RAIL - Preventive Maintenance Order | 26/01/2025 |  | 26/01/2025 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-BLD-MRLDCC Depot Control Centre | WES Wayside Department |  | DCC-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [{'item_no': '', 'material_no': '', 'description': '', 'required_quantity': '', 'unit_of_measurement': ''}] | [{'staff_id': '10007110', 'name': 'SYAHRUL AZWAN BIN MOHD YUSOF', 'plan_start_date_time': '26/01/2025 00:00:00', 'plan_end_date_time': '26/01/2025 04:00:00', 'total_hours': '4'}] | PM COMPLETED | UPS | Scheduled maintenance- |  |  | 26/01/2025 | 7110
[19 empty] | [] | [] | []
4000669552 | RAIL - Preventive Maintenance Order | 22/01/2025 |  | 22/01/2025 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLMKU Station Medan Tuanku | WES Wayside Department |  | MKU-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [{'staff_id': '10007222', 'name': 'MOHD RAZIF BIN RAZALI', 'plan_start_date_time': '22/01/2025 00:00:00', 'plan_end_date_time': '22/01/2025 04:00:00', 'total_hours': '4'}] | PM Completed | UPS | Scheduled maintenance- |  |  | 22/01/2025 | 7222
[19 empty] | [] | [] | []
[19 empty] | [] | [] | []
4000493784 | RAIL - Preventive Maintenance Order | 20/10/2022 |  | 20/10/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLRAN Station Raja Chulan | WES Wayside Department |  | RAN-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 20/10/2022 | 7111
4000493774 | RAIL - Preventive Maintenance Order | 18/10/2022 |  | 18/10/2022 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLIBI Station Imbi | WES Wayside Department |  | IBI-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 18/10/2022 | 7111
4000647402 | RAIL - Preventive Maintenance Order | 25/10/2024 |  | 25/10/2024 | 8021131201 | 12378429 | M7 | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-BLD-MRLOCC Operation Control Centre | WES Wayside Department |  | OCC-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] |  | UPS | Scheduled maintenance- |  | Check / Inspect- | 25/10/24
4000509057 | RAIL - Preventive Maintenance Order | 20/01/2023 |  | 20/01/2023 | 8021131201 |  |  | 3-Medium |  |  | PVM | WS20 | 0805 Rapid Rail StarRail (Monorail) | PRAL-MRL-WS-STN-MRLRAN Station Raja Chulan | WES Wayside Department |  | RAN-UPS Uninterruptable Power System |  | [{'operation_no': '0010', 'operation_text': 'Quarterly Inspection for UPS System'}] | [] | [] | [5 empty] | 20/01/2023 | 7111
[6 empty] | 12110781 | M7 | [11 empty] | [] | [] | []